## Sheet1
Part Number | ross section conductor | Norm | Conductor | Insulation | Sheath | Rated voltage | Diameter conductor | Insulation thickness | Diameter over insulation | Metallic screen mm2 | Diameter over screen | Outer diameter of cable | Cable weight | Max. pulling force | Min. bending radius | Resistance conductor | Electrical stress conductor | Electrical stress insulation | Capacitance | Reactance … | Reactance :. | Test voltage | Maximal short-circuit temperature | Maximal operating conductor temperature | Minimal temperature for laying | Minimal storage temperature | Operating temperature range
Units | mm2 |  |  |  |  | kV | mm | mm |  | Cross section mm2 | mm | [10 empty] | kV | °C | °C | °C | °C | °C
N2XS(FL)2Y | 1×150RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 | 14.4 | 18.00 | 53.4 | 95 | 59.2 | 67.00 | 5280.00 | 4.5 | 1.70 | 0.1588 | 6.56 | 2.14 | 0.119 | 0.215 | 0.155
N2XS(FL)2Y | 1×185RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 17.00 |  |  |  | 66.00 | 5450.00 |  | 1.70 | 0.13
N2XS(FL)2Y | 1×240RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 67.00 | 6000.00 |  | 1.70 | 0.10
N2XS(FL)2Y | 1×300RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 67.00 | 6500.00 |  | 1.70 | 0.08
N2XS(FL)2Y | 1×400RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 69.00 | 7300.00 |  | 1.70 | 0.06
N2XS(FL)2Y | 1×500RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 71.00 | 8350.00 |  | 1.80 | 0.05
N2XS(FL)2Y | 1×630RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 75.00 | 9920.00 |  | 1.90 | 0.04
N2XS(FL)2Y | 1×800RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 80.00 | 11740.00 |  | 2.00 | 0.03
N2XS(FL)2Y | 1×1000RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 84.00 | 13880.00 |  | 2.10 | 0.03
N2XS(FL)2Y | 1×1200RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 89.00 | 16090.00 |  | 2.20 | 0.02
N2XS(FL)2Y | 1×1400RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 94.00 | 18040.00 |  | 2.30 | 0.02
N2XS(FL)2Y | 1×1600RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 98.00 | 20290.00 |  | 2.40 | 0.02
N2XS(FL)2Y | 1×1800RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 102.00 | 22700.00 |  | 2.50 | 0.02
N2XS(FL)2Y | 1×2000RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 103.00 | 24270.00 |  | 2.60 | 0.02
N2XS(FL)2Y | 1×2500RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 112.00 | 29830.00 |  | 2.80 | 0.01
N2XS(FL)2Y | 1×3000RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 121.00 | 35960.00 |  | 3.00 | 0.01
NA2XS(FL)2Y | 1×150RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 18.00 |  |  |  | 67.00 | 4350.00 |  | 1.70 | 0.26
NA2XS(FL)2Y | 1×185RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 17.00 |  |  |  | 66.00 | 4330.00 |  | 1.70 | 0.21
NA2XS(FL)2Y | 1×240RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 67.00 | 4490.00 |  | 1.70 | 0.16
NA2XS(FL)2Y | 1×300RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 67.00 | 4600.00 |  | 1.70 | 0.13
NA2XS(FL)2Y | 1×400RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 68.00 | 4820.00 |  | 1.70 | 0.10
NA2XS(FL)2Y | 1×500RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 70.00 | 5210.00 |  | 1.80 | 0.08
NA2XS(FL)2Y | 1×630RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 74.00 | 5910.00 |  | 1.90 | 0.06
NA2XS(FL)2Y | 1×800RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 78.00 | 6610.00 |  | 2.00 | 0.05
NA2XS(FL)2Y | 1×1000RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 84.00 | 7540.00 |  | 2.10 | 0.04
NA2XS(FL)2Y | 1×1200RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 88.00 | 8440.00 |  | 2.20 | 0.04
NA2XS(FL)2Y | 1×1200RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 91.00 | 8710.00 |  | 2.30 | 0.03
NA2XS(FL)2Y | 1×1400RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 93.00 | 9420.00 |  | 2.30 | 0.03
NA2XS(FL)2Y | 1×1600RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 97.00 | 10240.00 |  | 2.40 | 0.02
NA2XS(FL)2Y | 1×1800RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 101.00 | 11200.00 |  | 2.50 | 0.02
NA2XS(FL)2Y | 1×2000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 103.00 | 11830.00 |  | 2.60 | 0.02
NA2XS(FL)2Y | 1×2500RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 110.00 | 13610.00 |  | 2.80 | 0.02
NA2XS(FL)2Y | 1×3000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 119.00 | 16180.00 |  | 3.00 | 0.01
N2X(F)KLD2Y | 1×240RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 86.00 | 7040.00 |  | 2.20 | 0.10
N2X(F)KLD2Y | 1×300RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 86.00 | 7550.00 |  | 2.20 | 0.08
N2X(F)KLD2Y | 1×400RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 88.00 | 8380.00 |  | 2.20 | 0.06
N2X(F)KLD2Y | 1×500RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 91.00 | 9530.00 |  | 2.20 | 0.05
N2X(F)KLD2Y | 1×630RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 95.00 | 11190.00 |  | 2.40 | 0.04
N2X(F)KLD2Y | 1×800RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 100.00 | 13160.00 |  | 2.50 | 0.03
N2X(F)KLD2Y | 1×1000RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 104.00 | 15380.00 |  | 2.60 | 0.03
N2X(F)KLD2Y | 1×1200RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 110.00 | 17790.00 |  | 2.80 | 0.02
N2X(F)KLD2Y | 1×1400RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 115.00 | 19870.00 |  | 2.90 | 0.02
N2X(F)KLD2Y | 1×1600RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 119.00 | 22210.00 |  | 3.00 | 0.02
N2X(F)KLD2Y | 1×1800RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 122.00 | 24720.00 |  | 3.10 | 0.02
N2X(F)KLD2Y | 1×2000RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 124.00 | 26340.00 |  | 3.10 | 0.02
N2X(F)KLD2Y | 1×2500RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 134.00 | 31880.00 |  | 3.30 | 0.01
NA2X(F)KLD2Y | 1×240RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 86.00 | 5510.00 |  | 2.10 | 0.16
NA2X(F)KLD2Y | 1×300RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 86.00 | 5630.00 |  | 2.20 | 0.13
NA2X(F)KLD2Y | 1×400RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 87.00 | 5750.00 |  | 2.20 | 0.10
NA2X(F)KLD2Y | 1×500RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 90.00 | 6380.00 |  | 2.30 | 0.08
NA2X(F)KLD2Y | 1×630RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 94.00 | 7000.00 |  | 2.40 | 0.06
NA2X(F)KLD2Y | 1×800RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 98.00 | 7960.00 |  | 2.50 | 0.05
NA2X(F)KLD2Y | 1×1000RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 103.00 | 9030.00 |  | 2.60 | 0.04
NA2X(F)KLD2Y | 1×1200RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 112.00 | 10450.00 |  | 2.80 | 0.03
NA2X(F)KLD2Y | 1×1400RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 114.00 | 11190.00 |  | 2.80 | 0.03
NA2X(F)KLD2Y | 1×1600RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 118.00 | 12140.00 |  | 2.90 | 0.02
NA2X(F)KLD2Y | 1×1800RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 122.00 | 13220.00 |  | 3.10 | 0.02
NA2X(F)KLD2Y | 1×2000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 124.00 | 13900.00 |  | 3.10 | 0.02
NA2X(F)KLD2Y | 1×2500RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 133.00 | 15970.00 |  | 3.30 | 0.02
NA2X(F)KLD2Y | 1×3000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 141.00 | 18720.00 |  | 3.50 | 0.01
N2X(F)K2Y | 1×150RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 18.00 |  |  |  | 67.00 | 8300.00 |  | 1.40 | 0.16
N2X(F)K2Y | 1×185RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 17.00 |  |  |  | 66.00 | 8400.00 |  | 1.30 | 0.13
N2X(F)K2Y | 1×240RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 67.00 | 9030.00 |  | 1.40 | 0.10
N2X(F)K2Y | 1×300RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 67.00 | 9540.00 |  | 1.40 | 0.08
N2X(F)K2Y | 1×400RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 69.00 | 10410.00 |  | 1.40 | 0.06
N2X(F)K2Y | 1×500RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 71.00 | 11590.00 |  | 1.40 | 0.05
N2X(F)K2Y | 1×630RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 75.00 | 13470.00 |  | 1.50 | 0.04
N2X(F)K2Y | 1×800RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 80.00 | 15590.00 |  | 1.60 | 0.03
N2X(F)K2Y | 1×1000RM | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 84.00 | 17980.00 |  | 1.70 | 0.03
N2X(F)K2Y | 1×1200RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 89.00 | 20530.00 |  | 1.80 | 0.02
N2X(F)K2Y | 1×1400RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 94.00 | 22780.00 |  | 1.90 | 0.02
N2X(F)K2Y | 1×1600RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 98.00 | 25280.00 |  | 2.00 | 0.02
N2X(F)K2Y | 1×1800RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 102.00 | 27940.00 |  | 2.00 | 0.02
N2X(F)K2Y | 1×2000RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 103.00 | 29610.00 |  | 2.10 | 0.02
N2X(F)K2Y | 1×2500RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 112.00 | 35400.00 |  | 2.20 | 0.01
N2X(F)K2Y | 1×3000RMS | Acc. VDE 0276-632 | Copper | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 121.00 | 42420.00 |  | 2.40 | 0.01
NA2X(F)K2Y | 1×150RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 18.00 |  |  |  | 67.00 | 7360.00 |  | 1.30 | 0.26
NA2X(F)K2Y | 1×185RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 17.00 |  |  |  | 66.00 | 7270.00 |  | 1.30 | 0.21
NA2X(F)K2Y | 1×240RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 16.50 |  |  |  | 67.00 | 7480.00 |  | 1.30 | 0.16
NA2X(F)K2Y | 1×300RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 15.50 |  |  |  | 67.00 | 7600.00 |  | 1.30 | 0.13
NA2X(F)K2Y | 1×400RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 68.00 | 7890.00 |  | 1.40 | 0.10
NA2X(F)K2Y | 1×500RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 70.00 | 8400.00 |  | 1.40 | 0.08
NA2X(F)K2Y | 1×630RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 74.00 | 9390.00 |  | 1.50 | 0.06
NA2X(F)K2Y | 1×800RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 78.00 | 10350.00 |  | 1.60 | 0.05
NA2X(F)K2Y | 1×1000RM | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 84.00 | 11620.00 |  | 1.70 | 0.04
NA2X(F)K2Y | 1×1200RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 91.00 | 13250.00 |  | 1.80 | 0.03
NA2X(F)K2Y | 1×1400RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 93.00 | 14100.00 |  | 1.90 | 0.03
NA2X(F)K2Y | 1×1600RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 97.00 | 15160.00 |  | 1.90 | 0.02
NA2X(F)K2Y | 1×1800RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 101.00 | 16410.00 |  | 2.00 | 0.02
NA2X(F)K2Y | 1×2000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.00 |  |  |  | 103.00 | 17160.00 |  | 2.10 | 0.02
NA2X(F)K2Y | 1×2500RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 110.00 | 19420.00 |  | 2.20 | 0.02
NA2X(F)K2Y | 1×3000RMS | Acc. VDE 0276-632 | Aluminum | XLPE | PE | 64/110 |  | 14.50 |  |  |  | 119.00 | 22550.00 |  | 2.40 | 0.01