## Sheet1
Part Number | Conductor | Insulation | CUScreen | Sheath | Number of cores and cross-section | Rated voltage | Test voltage | Maximal short-circuit temperature | Maximal operating conductor temperature | Minimal temperature for laying | Minimal storage temperature | Operating temperature range | Colour of insulation | Colour of sheath | Self-extinguishing of single cable | CPR class | Packaging | RoHS/REACH | Bending radius | Shape of conductor | Nominal insulation thickness | Nominal sheath thickness | Outer diameter (approx.) | Weight (approx.) | Maximum resistance of conductor
Units |  |  |  |  | mm2 | kV | kV | °C | °C | °C | °C | °C | [8 empty] | mm | mm | mm | kg/km | Ohm/km
NYY | CU | PVC | No | PVC | 1x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 6.5 | 73 | 12.1
NYY | CU | PVC | No | PVC | 1x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 7 | 88 | 7.41
NYY | CU | PVC | No | PVC | 1x4.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 8 | 122 | 4.61
NYY | CU | PVC | No | PVC | 1x6.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 8.5 | 150 | 3.08
NYY | CU | PVC | No | PVC | 1x10.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 9 | 205 | 1.83
NYY | CU | PVC | No | PVC | 1x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 11 | 249 | 1.15
NYY | CU | PVC | No | PVC | 1x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 11 | 255 | 1.15
NYY | CU | PVC | No | PVC | 1x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 12 | 366 | 0.727
NYY | CU | PVC | No | PVC | 1x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 14 | 471 | 0.524
NYY | CU | PVC | No | PVC | 1x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 15 | 609 | 0.387
NYY | CU | PVC | No | PVC | 1x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 17 | 823 | 0.268
NYY | CU | PVC | No | PVC | 1x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 19 | 1100 | 0.193
NYY | CU | PVC | No | PVC | 1x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 20 | 1340 | 0.153
NYY | CU | PVC | No | PVC | 1x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 22 | 1640 | 0.124
NYY | CU | PVC | No | PVC | 1x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.8 | 25 | 2024 | 0.0991
NYY | CU | PVC | No | PVC | 1x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 1.8 | 27 | 2601 | 0.0754
NYY | CU | PVC | No | PVC | 1x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.4 | 1.9 | 30 | 3232 | 0.0601
NYY | CU | PVC | No | PVC | 1x400 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.6 | 2 | 34 | 4093 | 0.047
NYY | CU | PVC | No | PVC | 1x500 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.8 | 2.1 | 37 | 5184 | 0.0366
NYY | CU | PVC | No | PVC | 2x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 11 | 164 | 12.1
NYY | CU | PVC | No | PVC | 2x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 12 | 200 | 7.41
NYY | CU | PVC | No | PVC | 2x4.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 13 | 275 | 4.61
NYY | CU | PVC | No | PVC | 2x6.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 14 | 338 | 3.08
NYY | CU | PVC | No | PVC | 2x10.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 16 | 457 | 1.83
NYY | CU | PVC | No | PVC | 2x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 19 | 714 | 1.15
NYY | CU | PVC | No | PVC | 2x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 20 | 743 | 1.15
NYY | CU | PVC | No | PVC | 2x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 23 | 1059 | 0.727
NYY | CU | PVC | No | PVC | 2x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 25 | 1349 | 0.524
NYY | CU | PVC | No | PVC | 3x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 11 | 184 | 12.1
NYY | CU | PVC | No | PVC | 3x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 12 | 226 | 7.41
NYY | CU | PVC | No | PVC | 3x4.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 14 | 318 | 4.61
NYY | CU | PVC | No | PVC | 3x6.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 15 | 403 | 3.08
NYY | CU | PVC | No | PVC | 3x10.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 17 | 557 | 1.83
NYY | CU | PVC | No | PVC | 3x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 20 | 872 | 1.15
NYY | CU | PVC | No | PVC | 3x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 21 | 902 | 1.15
NYY | CU | PVC | No | PVC | 3x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 24 | 1303 | 0.727
NYY | CU | PVC | No | PVC | 3x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 25 | 1532 | 0.524
NYY | CU | PVC | No | PVC | 3x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.8 | 28 | 1966 | 0.387
NYY | CU | PVC | No | PVC | 3x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 31 | 2685 | 0.268
NYY | CU | PVC | No | PVC | 3x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.1 | 36 | 3582 | 0.193
NYY | CU | PVC | No | PVC | 3x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 4351 | 0.153
NYY | CU | PVC | No | PVC | 3x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.3 | 43 | 5356 | 0.124
NYY | CU | PVC | No | PVC | 3x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.5 | 47 | 6582 | 0.0991
NYY | CU | PVC | No | PVC | 3x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.7 | 53 | 8519 | 0.0754
NYY | CU | PVC | No | PVC | 3x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.4 | 2.9 | 58 | 10504 | 0.0601
NYY | CU | PVC | No | PVC | 3x25+16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV/RE | 1.2/1.0 | 1.8 | 25 | 1482 | 0.727
NYY | CU | PVC | No | PVC | 3x35+16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RE | 1.2/1.0 | 1.8 | 27 | 1786 | 0.524
NYY | CU | PVC | No | PVC | 3x50+25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.4/1.2 | 1.9 | 30 | 2364 | 0.387
NYY | CU | PVC | No | PVC | 3x70+35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4/1.2 | 2 | 34 | 3133 | 0.268
NYY | CU | PVC | No | PVC | 3x95+50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.2 | 39 | 4196 | 0.193
NYY | CU | PVC | No | PVC | 3x120+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.3 | 42 | 5224 | 0.153
NYY | CU | PVC | No | PVC | 3x150+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8/1.4 | 2.4 | 47 | 6210 | 0.124
NYY | CU | PVC | No | PVC | 3x185+95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.0/1.6 | 2.6 | 51 | 7712 | 0.0991
NYY | CU | PVC | No | PVC | 3x240+120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2/1.6 | 2.8 | 58 | 9931 | 0.0754
NYY | CU | PVC | No | PVC | 3x300+150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.4/1.8 | 3 | 64 | 12265 | 0.0601
NYY | CU | PVC | No | PVC | 4x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 12 | 214 | 12.1
NYY | CU | PVC | No | PVC | 4x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 13 | 269 | 7.41
NYY | CU | PVC | No | PVC | 4x4.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 15 | 374 | 4.61
NYY | CU | PVC | No | PVC | 4x6.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 16 | 491 | 3.08
NYY | CU | PVC | No | PVC | 4x10.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 18 | 669 | 1.83
NYY | CU | PVC | No | PVC | 4x10 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 21 | 818 | 1.83
NYY | CU | PVC | No | PVC | 4x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 22 | 1062 | 1.15
NYY | CU | PVC | No | PVC | 4x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.2 | 26 | 1606 | 0.727
NYY | CU | PVC | No | PVC | 4x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 27 | 1962 | 0.524
NYY | CU | PVC | No | PVC | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 31 | 2594 | 0.387
NYY | CU | PVC | No | PVC | 4x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 34 | 3492 | 0.268
NYY | CU | PVC | No | PVC | 4x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 39 | 4668 | 0.193
NYY | CU | PVC | No | PVC | 4x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 43 | 5754 | 0.153
NYY | CU | PVC | No | PVC | 4x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.5 | 48 | 7026 | 0.124
NYY | CU | PVC | No | PVC | 4x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.7 | 53 | 8715 | 0.0991
NYY | CU | PVC | No | PVC | 4x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.9 | 59 | 11195 | 0.0754
NYY | CU | PVC | No | PVC | 4x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.4 | 3.1 | 65 | 13815 | 0.0601
NYY | CU | PVC | No | PVC | 5x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 13 | 255 | 12.1
NYY | CU | PVC | No | PVC | 5x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 14 | 327 | 7.41
NYY | CU | PVC | No | PVC | 5x4.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 16 | 460 | 4.61
NYY | CU | PVC | No | PVC | 5x6.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 17 | 598 | 3.08
NYY | CU | PVC | No | PVC | 5x10.0 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 19 | 842 | 1.83
NYY | CU | PVC | No | PVC | 5x10 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 22 | 975 | 1.83
NYY | CU | PVC | No | PVC | 5x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 1275 | 1.15
NYY | CU | PVC | No | PVC | 5x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 25 | 1315 | 1.15
NYY | CU | PVC | No | PVC | 5x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 29 | 1960 | 0.727
NYY | CU | PVC | No | PVC | 5x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.9 | 32 | 2584 | 0.524
NYY | CU | PVC | No | PVC | 5x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 2 | 37 | 3419 | 0.387
NYY | CU | PVC | No | PVC | 5x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 35 | 3258 | 0.387
NYY | CU | PVC | No | PVC | 5x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 2.2 | 42 | 4689 | 0.268
NYY | CU | PVC | No | PVC | 5x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.2 | 40 | 4411 | 0.268
NYY | CU | PVC | No | PVC | 5x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 2.4 | 48 | 6354 | 0.193
NYY | CU | PVC | No | PVC | 5x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 5944 | 0.193
NYY | CU | PVC | No | PVC | 5x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 2.5 | 52 | 7727 | 0.153
NYY | CU | PVC | No | PVC | 5x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.5 | 49 | 7255 | 0.153
NYY | CU | PVC | No | PVC | 7x1.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 13 | 301 | 12.1
NYY | CU | PVC | No | PVC | 7x2.5 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable coils/cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.8 | 1.8 | 15 | 388 | 7.41
NYCWY | CU | PVC | Yes | PVC | 2x10/10 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 19 | 670 | 1.83
NYCWY | CU | PVC | Yes | PVC | 2x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 21 | 890 | 1.15
NYCWY | CU | PVC | Yes | PVC | 3x10/10 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 20 | 773 | 1.83
NYCWY | CU | PVC | Yes | PVC | 3x10/10 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 21 | 817 | 1.83
NYCWY | CU | PVC | Yes | PVC | 3x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 22 | 1045 | 1.15
NYCWY | CU | PVC | Yes | PVC | 3x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 22 | 1085 | 1.15
NYCWY | CU | PVC | Yes | PVC | 3x25/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 1490 | 0.727
NYCWY | CU | PVC | Yes | PVC | 3x25/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 1582 | 0.727
NYCWY | CU | PVC | Yes | PVC | 3x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 26 | 1729 | 0.524
NYCWY | CU | PVC | Yes | PVC | 3x35/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 26 | 1913 | 0.524
NYCWY | CU | PVC | Yes | PVC | 3x50/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 29 | 2272 | 0.387
NYCWY | CU | PVC | Yes | PVC | 3x50/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 30 | 2498 | 0.387
NYCWY | CU | PVC | Yes | PVC | 3x70/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 33 | 3128 | 0.268
NYCWY | CU | PVC | Yes | PVC | 3x70/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 34 | 3473 | 0.268
NYCWY | CU | PVC | Yes | PVC | 3x95/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 4177 | 0.193
NYCWY | CU | PVC | Yes | PVC | 3x95/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 4640 | 0.193
NYCWY | CU | PVC | Yes | PVC | 3x120/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 41 | 5168 | 0.153
NYCWY | CU | PVC | Yes | PVC | 3x120/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 41 | 5674 | 0.153
NYCWY | CU | PVC | Yes | PVC | 3x150/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.4 | 46 | 6193 | 0.124
NYCWY | CU | PVC | Yes | PVC | 3x150/150 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.4 | 47 | 6982 | 0.124
NYCWY | CU | PVC | Yes | PVC | 3x185/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.6 | 50 | 7689 | 0.0991
NYCWY | CU | PVC | Yes | PVC | 3x185/185 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.6 | 51 | 8609 | 0.0991
NYCWY | CU | PVC | Yes | PVC | 3x240/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.8 | 56 | 9950 | 0.0754
NYCWY | CU | PVC | Yes | PVC | 4x10/10 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 21 | 903 | 1.83
NYCWY | CU | PVC | Yes | PVC | 4x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 1237 | 1.15
NYCWY | CU | PVC | Yes | PVC | 4x25/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 28 | 1801 | 0.727
NYCWY | CU | PVC | Yes | PVC | 4x25/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 28 | 1886 | 0.727
NYCWY | CU | PVC | Yes | PVC | 4x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 28 | 2156 | 0.524
NYCWY | CU | PVC | Yes | PVC | 4x35/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 28 | 2333 | 0.524
NYCWY | CU | PVC | Yes | PVC | 4x50/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 33 | 2944 | 0.387
NYCWY | CU | PVC | Yes | PVC | 4x50/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 34 | 3171 | 0.387
NYCWY | CU | PVC | Yes | PVC | 4x70/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 36 | 3932 | 0.268
NYCWY | CU | PVC | Yes | PVC | 4x70/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 37 | 4277 | 0.268
NYCWY | CU | PVC | Yes | PVC | 4x95/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 42 | 5276 | 0.193
NYCWY | CU | PVC | Yes | PVC | 4x95/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 42 | 5488 | 0.193
NYCWY | CU | PVC | Yes | PVC | 4x95/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 42 | 5740 | 0.193
NYCWY | CU | PVC | Yes | PVC | 4x120/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 46 | 6571 | 0.153
NYCWY | CU | PVC | Yes | PVC | 4x120/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 46 | 7077 | 0.153
NYCWY | CU | PVC | Yes | PVC | 4x150/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.6 | 51 | 7883 | 0.124
NYCWY | CU | PVC | Yes | PVC | 4x185/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.8 | 56 | 9892 | 0.0991
NYCWY | CU | PVC | Yes | PVC | 4x185/185 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.8 | 57 | 10813 | 0.0991
NYCWY | CU | PVC | Yes | PVC | 4x240/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 3 | 62 | 12658 | 0.0754
NY2Y | CU | PVC | No | PE | 1x10 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 10 | 157 | 1.83
NY2Y | CU | PVC | No | PE | 1x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 11 | 219 | 1.15
NY2Y | CU | PVC | No | PE | 1x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 12 | 329 | 0.727
NY2Y | CU | PVC | No | PE | 1x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 14 | 429 | 0.524
NY2Y | CU | PVC | No | PE | 1x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 15 | 565 | 0.387
NY2Y | CU | PVC | No | PE | 1x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 17 | 772 | 0.268
NY2Y | CU | PVC | No | PE | 1x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 19 | 1042 | 0.193
NY2Y | CU | PVC | No | PE | 1x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 20 | 1278 | 0.153
NY2Y | CU | PVC | No | PE | 1x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 22 | 1571 | 0.124
NY2Y | CU | PVC | No | PE | 1x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.8 | 25 | 1947 | 0.0991
NY2Y | CU | PVC | No | PE | 1x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 1.8 | 27 | 2514 | 0.0754
NY2Y | CU | PVC | No | PE | 1x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.4 | 1.9 | 30 | 3130 | 0.0601
NY2Y | CU | PVC | No | PE | 1x400 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.6 | 2 | 34 | 3972 | 0.047
NY2Y | CU | PVC | No | PE | 1x500 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.8 | 2.1 | 37 | 5043 | 0.0366
NY2Y | CU | PVC | No | PE | 3x10 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 18 | 589 | 1.83
NY2Y | CU | PVC | No | PE | 3x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 20 | 810 | 1.15
NY2Y | CU | PVC | No | PE | 3x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 24 | 1227 | 0.727
NY2Y | CU | PVC | No | PE | 3x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 25 | 1464 | 0.524
NY2Y | CU | PVC | No | PE | 3x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.8 | 28 | 1887 | 0.387
NY2Y | CU | PVC | No | PE | 3x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 31 | 2584 | 0.268
NY2Y | CU | PVC | No | PE | 3x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.1 | 36 | 3448 | 0.193
NY2Y | CU | PVC | No | PE | 3x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 4199 | 0.153
NY2Y | CU | PVC | No | PE | 3x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.3 | 43 | 5178 | 0.124
NY2Y | CU | PVC | No | PE | 3x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.5 | 47 | 6381 | 0.0991
NY2Y | CU | PVC | No | PE | 3x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.7 | 53 | 8264 | 0.0754
NY2Y | CU | PVC | No | PE | 3x35+16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RE | 1.2/1.0 | 1.8 | 27 | 1698 | 0.524
NAYY | CU | PVC | No | PVC | 1x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 11 | 153 | 1.91
NAYY | AL | PVC | No | PVC | 1x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 12 | 196 | 1.2
NAYY | AL | PVC | No | PVC | 1x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 12 | 213 | 1.2
NAYY | AL | PVC | No | PVC | 1x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 13 | 236 | 0.868
NAYY | AL | PVC | No | PVC | 1x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 14 | 256 | 0.868
NAYY | AL | PVC | No | PVC | 1x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 15 | 322 | 0.641
NAYY | AL | PVC | No | PVC | 1x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 17 | 406 | 0.443
NAYY | AL | PVC | No | PVC | 1x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 19 | 519 | 0.32
NAYY | AL | PVC | No | PVC | 1x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 20 | 610 | 0.253
NAYY | AL | PVC | No | PVC | 1x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 22 | 738 | 0.206
NAYY | AL | PVC | No | PVC | 1x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.8 | 25 | 897 | 0.164
NAYY | AL | PVC | No | PVC | 1x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 1.8 | 27 | 1106 | 0.125
NAYY | AL | PVC | No | PVC | 1x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.4 | 1.9 | 30 | 1371 | 0.1
NAYY | AL | PVC | No | PVC | 1x400 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.6 | 2 | 34 | 1714 | 0.0778
NAYY | AL | PVC | No | PVC | 1x500 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.8 | 2.1 | 37 | 2135 | 0.0605
NAYY | AL | PVC | No | PVC | 1x630 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.8 | 2.2 | 41 | 2631 | 0.0469
NAYY | AL | PVC | No | PVC | 2x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 19 | 526 | 1.91
NAYY | AL | PVC | No | PVC | 3x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 20 | 586 | 1.91
NAYY | AL | PVC | No | PVC | 3x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 24 | 841 | 1.2
NAYY | AL | PVC | No | PVC | 3x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 27 | 1022 | 0.868
NAYY | AL | PVC | No | PVC | 3x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.8 | 28 | 1094 | 0.641
NAYY | AL | PVC | No | PVC | 3x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 31 | 1428 | 0.443
NAYY | AL | PVC | No | PVC | 3x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.1 | 36 | 1835 | 0.32
NAYY | AL | PVC | No | PVC | 3x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 2150 | 0.253
NAYY | AL | PVC | No | PVC | 3x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.3 | 43 | 2633 | 0.206
NAYY | AL | PVC | No | PVC | 3x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.5 | 47 | 3183 | 0.164
NAYY | AL | PVC | No | PVC | 3x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.7 | 53 | 4048 | 0.125
NAYY | AL | PVC | No | PVC | 3x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.4 | 2.9 | 58 | 4887 | 0.1
NAYY | AL | PVC | No | PVC | 3x35+16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2/1.0 | 1.8 | 27 | 1081 | 0.868
NAYY | AL | PVC | No | PVC | 3x50+25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.4/1.2 | 1.9 | 30 | 1338 | 0.641
NAYY | AL | PVC | No | PVC | 3x70+35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.4/1.2 | 2 | 34 | 1707 | 0.443
NAYY | AL | PVC | No | PVC | 3x95+50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.2 | 39 | 2158 | 0.32
NAYY | AL | PVC | No | PVC | 3x120+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.3 | 42 | 2603 | 0.253
NAYY | AL | PVC | No | PVC | 3x150+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8/1.4 | 2.4 | 47 | 3069 | 0.206
NAYY | AL | PVC | No | PVC | 3x185+95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.0/1.6 | 2.6 | 51 | 3730 | 0.164
NAYY | AL | PVC | No | PVC | 3x240+120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2/1.6 | 2.8 | 58 | 4727 | 0.125
NAYY | AL | PVC | No | PVC | 4x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 22 | 679 | 1.91
NAYY | AL | PVC | No | PVC | 4x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 26 | 954 | 1.2
NAYY | AL | PVC | No | PVC | 4x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 989 | 1.2
NAYY | AL | PVC | No | PVC | 4x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 28 | 1160 | 0.868
NAYY | AL | PVC | No | PVC | 4x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 29 | 1207 | 0.868
NAYY | AL | PVC | No | PVC | 4x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 26 | 1064 | 0.868
NAYY | AL | PVC | No | PVC | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.4 | 1.9 | 32 | 1547 | 0.641
NAYY | AL | PVC | No | PVC | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 1.9 | 30 | 1340 | 0.641
NAYY | AL | PVC | No | PVC | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 31 | 1431 | 0.641
NAYY | AL | PVC | No | PVC | 4x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2.1 | 33 | 1706 | 0.443
NAYY | AL | PVC | No | PVC | 4x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 34 | 1816 | 0.443
NAYY | AL | PVC | No | PVC | 4x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.2 | 37 | 2216 | 0.32
NAYY | AL | PVC | No | PVC | 4x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 39 | 2338 | 0.32
NAYY | AL | PVC | No | PVC | 4x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.4 | 41 | 2695 | 0.253
NAYY | AL | PVC | No | PVC | 4x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 43 | 2818 | 0.253
NAYY | AL | PVC | No | PVC | 4x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.5 | 44 | 3152 | 0.206
NAYY | AL | PVC | No | PVC | 4x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.5 | 48 | 3396 | 0.206
NAYY | AL | PVC | No | PVC | 4x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2 | 2.7 | 50 | 3973 | 0.164
NAYY | AL | PVC | No | PVC | 4x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.7 | 53 | 4181 | 0.164
NAYY | AL | PVC | No | PVC | 4x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2.2 | 2.9 | 56 | 4935 | 0.125
NAYY | AL | PVC | No | PVC | 4x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.9 | 59 | 5234 | 0.125
NAYY | AL | PVC | No | PVC | 4x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.4 | 3.1 | 65 | 6343 | 0.1
NAYY | AL | PVC | No | PVC | 5x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 796 | 1.91
NAYY | AL | PVC | No | PVC | 5x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 28 | 1147 | 1.2
NAYY | AL | PVC | No | PVC | 5x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 29 | 1189 | 1.2
NAYY | AL | PVC | No | PVC | 5x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.9 | 31 | 1369 | 0.868
NAYY | AL | PVC | No | PVC | 5x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.9 | 32 | 1424 | 0.868
NAYY | AL | PVC | No | PVC | 5x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 2.1 | 37 | 2088 | 0.641
NAYY | AL | PVC | No | PVC | 5x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 35 | 1805 | 0.641
NAYY | AL | PVC | No | PVC | 5x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 2.2 | 42 | 2659 | 0.443
NAYY | AL | PVC | No | PVC | 5x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.2 | 40 | 2316 | 0.443
NAYY | AL | PVC | No | PVC | 5x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 2.4 | 48 | 3549 | 0.32
NAYY | AL | PVC | No | PVC | 5x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 3032 | 0.32
NAYY | AL | PVC | No | PVC | 5x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 2.5 | 52 | 4206 | 0.253
NAYY | AL | PVC | No | PVC | 5x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | – 35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.5 | 49 | 3586 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 2x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 21 | 651 | 1.91
NAYCWY | AL | PVC | Yes | PVC | 3x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 22 | 710 | 1.91
NAYCWY | AL | PVC | Yes | PVC | 3x25/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 969 | 1.2
NAYCWY | AL | PVC | Yes | PVC | 3x25/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 1028 | 1.2
NAYCWY | AL | PVC | Yes | PVC | 3x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 28 | 1173 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 3x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 26 | 1034 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 3x35/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 28 | 1235 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 3x35/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 26 | 1139 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 3x50/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 29 | 1309 | 0.641
NAYCWY | AL | PVC | Yes | PVC | 3x50/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 1.9 | 28 | 1377 | 0.641
NAYCWY | AL | PVC | Yes | PVC | 3x50/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 29 | 1441 | 0.641
NAYCWY | AL | PVC | Yes | PVC | 3x70/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 33 | 1740 | 0.443
NAYCWY | AL | PVC | Yes | PVC | 3x70/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2 | 34 | 1881 | 0.443
NAYCWY | AL | PVC | Yes | PVC | 3x70/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 34 | 1948 | 0.443
NAYCWY | AL | PVC | Yes | PVC | 3x95/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 2243 | 0.32
NAYCWY | AL | PVC | Yes | PVC | 3x95/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.2 | 38 | 2529 | 0.32
NAYCWY | AL | PVC | Yes | PVC | 3x120/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 41 | 2699 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 3x120/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.3 | 40 | 2915 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 3x120/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 41 | 3011 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 3x150/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.4 | 46 | 3242 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 3x150/150 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.4 | 44 | 3531 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 3x150/150 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.4 | 46 | 3674 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 3x185/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.6 | 50 | 3925 | 0.164
NAYCWY | AL | PVC | Yes | PVC | 3x185/185 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2 | 2.6 | 48 | 4313 | 0.164
NAYCWY | AL | PVC | Yes | PVC | 3x185/185 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.6 | 50 | 4492 | 0.164
NAYCWY | AL | PVC | Yes | PVC | 3x240/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.8 | 56 | 5018 | 0.125
NAYCWY | AL | PVC | Yes | PVC | 4x16/10 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 802 | 1.91
NAYCWY | AL | PVC | Yes | PVC | 4x16/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 808 | 1.91
NAYCWY | AL | PVC | Yes | PVC | 4x25/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 27 | 1090 | 1.2
NAYCWY | AL | PVC | Yes | PVC | 4x25/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 28 | 1141 | 1.2
NAYCWY | AL | PVC | Yes | PVC | 4x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 30 | 1327 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 4x35/16 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 1.8 | 28 | 1253 | 0.868
NAYCWY | AL | PVC | Yes | PVC | 4x50/25 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 33 | 1691 | 0.641
NAYCWY | AL | PVC | Yes | PVC | 4x50/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2 | 31 | 1637 | 0.641
NAYCWY | AL | PVC | Yes | PVC | 4x70/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2.1 | 35 | 2012 | 0.443
NAYCWY | AL | PVC | Yes | PVC | 4x70/35 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.1 | 36 | 2125 | 0.443
NAYCWY | AL | PVC | Yes | PVC | 4x95/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.3 | 39 | 2631 | 0.32
NAYCWY | AL | PVC | Yes | PVC | 4x95/50 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 41 | 2760 | 0.32
NAYCWY | AL | PVC | Yes | PVC | 4x95/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.3 | 42 | 3047 | 0.32
NAYCWY | AL | PVC | Yes | PVC | 4x120/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.4 | 44 | 3280 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 4x120/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 46 | 3407 | 0.253
NAYCWY | AL | PVC | Yes | PVC | 4x150/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.6 | 48 | 3870 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 4x150/70 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.6 | 51 | 4062 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 4x150/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.6 | 51 | 4297 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 4x150/150 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.6 | 48 | 4263 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 4x150/150 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.6 | 51 | 4455 | 0.206
NAYCWY | AL | PVC | Yes | PVC | 4x185/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2 | 2.8 | 53 | 4775 | 0.164
NAYCWY | AL | PVC | Yes | PVC | 4x185/95 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.8 | 56 | 4995 | 0.164
NAYCWY | AL | PVC | Yes | PVC | 4x240/120 | 0.6/1 | 4 | 160 | 70 | -5 | -35 | -35 - +70 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 3 | 62 | 6235 | 0.125
NAY2Y | AL | PVC | No | PE | 1x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 11 | 122 | 1.91
NAY2Y | AL | PVC | No | PE | 1x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 12 | 171 | 1.2
NAY2Y | AL | PVC | No | PE | 1x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 13 | 209 | 0.868
NAY2Y | AL | PVC | No | PE | 1x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 15 | 277 | 0.641
NAY2Y | AL | PVC | No | PE | 1x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 17 | 356 | 0.443
NAY2Y | AL | PVC | No | PE | 1x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 19 | 464 | 0.32
NAY2Y | AL | PVC | No | PE | 1x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 20 | 549 | 0.253
NAY2Y | AL | PVC | No | PE | 1x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 22 | 670 | 0.206
NAY2Y | AL | PVC | No | PE | 1x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.8 | 25 | 821 | 0.164
NAY2Y | AL | PVC | No | PE | 1x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 1.8 | 27 | 1035 | 0.125
NAY2Y | AL | PVC | No | PE | 1x300 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.4 | 1.9 | 30 | 1273 | 0.1
NAY2Y | AL | PVC | No | PE | 1x400 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.6 | 2 | 34 | 1598 | 0.0778
NAY2Y | AL | PVC | No | PE | 1x500 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.8 | 2.1 | 37 | 2001 | 0.0605
NAY2Y | AL | PVC | No | PE | 3x10 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 18 | 398 | 3.08
NAY2Y | AL | PVC | No | PE | 3x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 20 | 523 | 1.91
NAY2Y | AL | PVC | No | PE | 3x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 24 | 735 | 1.2
NAY2Y | AL | PVC | No | PE | 3x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 26 | 903 | 0.868
NAY2Y | AL | PVC | No | PE | 3x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 1.8 | 27 | 955 | 0.641
NAY2Y | AL | PVC | No | PE | 3x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2 | 31 | 1263 | 0.443
NAY2Y | AL | PVC | No | PE | 3x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.1 | 34 | 1625 | 0.32
NAY2Y | AL | PVC | No | PE | 3x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.2 | 37 | 1911 | 0.253
NAY2Y | AL | PVC | No | PE | 3x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.3 | 41 | 2329 | 0.206
NAY2Y | AL | PVC | No | PE | 3x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2 | 2.5 | 45 | 2821 | 0.164
NAY2Y | AL | PVC | No | PE | 3x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2.2 | 2.7 | 50 | 3573 | 0.125
NAY2Y | AL | PVC | No | PE | 3x35+16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2/1.0 | 1.8 | 27 | 981 | 0.868
NAY2Y | AL | PVC | No | PE | 3x50+25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.4/1.2 | 1.9 | 30 | 1222 | 0.641
NAY2Y | AL | PVC | No | PE | 3x70+35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.4/1.2 | 2 | 34 | 1582 | 0.443
NAY2Y | AL | PVC | No | PE | 3x95+50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.2 | 39 | 2004 | 0.32
NAY2Y | AL | PVC | No | PE | 3x120+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.4 | 2.3 | 42 | 2429 | 0.253
NAY2Y | AL | PVC | No | PE | 3x150+70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8/1.4 | 2.4 | 47 | 2854 | 0.206
NAY2Y | AL | PVC | No | PE | 3x185+95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.0/1.6 | 2.6 | 51 | 3492 | 0.164
NAY2Y | AL | PVC | No | PE | 3x240+120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2/1.6 | 2.8 | 58 | 4437 | 0.125
NAY2Y | AL | PVC | No | PE | 4x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 22 | 611 | 1.91
NAY2Y | AL | PVC | No | PE | 4x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 23 | 649 | 1.91
NAY2Y | AL | PVC | No | PE | 4x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 26 | 873 | 1.2
NAY2Y | AL | PVC | No | PE | 4x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 26 | 906 | 1.2
NAY2Y | AL | PVC | No | PE | 4x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 28 | 1071 | 0.868
NAY2Y | AL | PVC | No | PE | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 1.9 | 30 | 1238 | 0.641
NAY2Y | AL | PVC | No | PE | 4x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 1.9 | 31 | 1324 | 0.641
NAY2Y | AL | PVC | No | PE | 4x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2.1 | 33 | 1591 | 0.443
NAY2Y | AL | PVC | No | PE | 4x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.2 | 37 | 2068 | 0.32
NAY2Y | AL | PVC | No | PE | 4x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.4 | 41 | 2518 | 0.253
NAY2Y | AL | PVC | No | PE | 4x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.8 | 2.5 | 45 | 3013 | 0.206
NAY2Y | AL | PVC | No | PE | 4x150 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.8 | 2.5 | 48 | 3183 | 0.206
NAY2Y | AL | PVC | No | PE | 4x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2 | 2.7 | 50 | 3732 | 0.164
NAY2Y | AL | PVC | No | PE | 4x185 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2 | 2.7 | 53 | 3928 | 0.164
NAY2Y | AL | PVC | No | PE | 4x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 2.2 | 2.9 | 56 | 4648 | 0.125
NAY2Y | AL | PVC | No | PE | 4x240 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 2.2 | 2.9 | 59 | 4929 | 0.125
NAY2Y | AL | PVC | No | PE | 5x16 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1 | 1.8 | 24 | 721 | 1.91
NAY2Y | AL | PVC | No | PE | 5x25 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.8 | 28 | 1059 | 1.2
NAY2Y | AL | PVC | No | PE | 5x35 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 1.2 | 1.9 | 31 | 1320 | 0.868
NAY2Y | AL | PVC | No | PE | 5x50 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2 | 35 | 1661 | 0.641
NAY2Y | AL | PVC | No | PE | 5x70 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.2 | 40 | 2137 | 0.443
NAY2Y | AL | PVC | No | PE | 5x95 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 2816 | 0.32
NAY2Y | AL | PVC | No | PE | 5x120 | 0.6/1 | 4 | ≤ 300 mm2: +160, > 300 mm2: +140 | 70 | -5 | -35 | - 35 - +70 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.5 | 49 | 3342 | 0.253
N2XY | CU | XLPE | No | PVC | 1x10 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 9 | 166 | 1.83
N2XY | CU | XLPE | No | PVC | 1x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 10 | 229 | 1.15
N2XY | CU | XLPE | No | PVC | 1x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 12 | 336 | 0.727
N2XY | CU | XLPE | No | PVC | 1x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 13 | 436 | 0.524
N2XY | CU | XLPE | No | PVC | 1x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 14 | 562 | 0.387
N2XY | CU | XLPE | No | PVC | 1x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 16 | 774 | 0.268
N2XY | CU | XLPE | No | PVC | 1x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 18 | 1027 | 0.193
N2XY | CU | XLPE | No | PVC | 1x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 20 | 1267 | 0.153
N2XY | CU | XLPE | No | PVC | 1x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 22 | 1555 | 0.124
N2XY | CU | XLPE | No | PVC | 1x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 24 | 1922 | 0.0991
N2XY | CU | XLPE | No | PVC | 1x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.7 | 1.8 | 26 | 2471 | 0.0754
N2XY | CU | XLPE | No | PVC | 1x300 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 29 | 3055 | 0.0601
N2XY | CU | XLPE | No | PVC | 1x400 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.9 | 32 | 3880 | 0.047
N2XY | CU | XLPE | No | PVC | 1x500 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 2 | 36 | 4938 | 0.0366
N2XY | CU | XLPE | No | PVC | 3x10 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 17 | 581 | 1.83
N2XY | CU | XLPE | No | PVC | 3x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 19 | 800 | 1.15
N2XY | CU | XLPE | No | PVC | 3x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 23 | 1193 | 0.727
N2XY | CU | XLPE | No | PVC | 3x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 26 | 1553 | 0.524
N2XY | CU | XLPE | No | PVC | 3x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.8 | 26 | 1815 | 0.387
N2XY | CU | XLPE | No | PVC | 3x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 1.9 | 30 | 2519 | 0.268
N2XY | CU | XLPE | No | PVC | 3x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 3319 | 0.193
N2XY | CU | XLPE | No | PVC | 3x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.1 | 37 | 4089 | 0.153
N2XY | CU | XLPE | No | PVC | 3x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.3 | 41 | 5077 | 0.124
N2XY | CU | XLPE | No | PVC | 3x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 6233 | 0.0991
N2XY | CU | XLPE | No | PVC | 3x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.6 | 51 | 8067 | 0.0754
N2XY | CU | XLPE | No | PVC | 3x25+16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV/RE | 0.9/0.7 | 1.8 | 24 | 1357 | 0.727
N2XY | CU | XLPE | No | PVC | 3x35+16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RE | 0.9/0.7 | 1.8 | 26 | 1658 | 0.524
N2XY | CU | XLPE | No | PVC | 3x50+25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.0/0.9 | 1.8 | 29 | 2170 | 0.387
N2XY | CU | XLPE | No | PVC | 3x70+35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/0.9 | 1.9 | 32 | 2932 | 0.268
N2XY | CU | XLPE | No | PVC | 3x95+50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/1.0 | 2.1 | 37 | 3897 | 0.193
N2XY | CU | XLPE | No | PVC | 3x120+70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2/1.1 | 2.2 | 40 | 4865 | 0.153
N2XY | CU | XLPE | No | PVC | 3x150+70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4/1.1 | 2.3 | 45 | 5862 | 0.124
N2XY | CU | XLPE | No | PVC | 3x185+95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.1 | 2.5 | 49 | 7293 | 0.0991
N2XY | CU | XLPE | No | PVC | 3x240+120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7/1.2 | 2.7 | 56 | 9407 | 0.0754
N2XY | CU | XLPE | No | PVC | 4x10 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 18 | 698 | 1.83
N2XY | CU | XLPE | No | PVC | 4x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 21 | 974 | 1.15
N2XY | CU | XLPE | No | PVC | 4x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.7 | 1.8 | 21 | 995 | 1.15
N2XY | CU | XLPE | No | PVC | 4x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 25 | 1469 | 0.727
N2XY | CU | XLPE | No | PVC | 4x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 0.9 | 1.8 | 26 | 1818 | 0.524
N2XY | CU | XLPE | No | PVC | 4x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.9 | 29 | 2354 | 0.387
N2XY | CU | XLPE | No | PVC | 4x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 3268 | 0.268
N2XY | CU | XLPE | No | PVC | 4x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 37 | 4341 | 0.193
N2XY | CU | XLPE | No | PVC | 4x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.3 | 41 | 5429 | 0.153
N2XY | CU | XLPE | No | PVC | 4x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.4 | 46 | 6637 | 0.124
N2XY | CU | XLPE | No | PVC | 4x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.6 | 51 | 8188 | 0.0991
N2XY | CU | XLPE | No | PVC | 4x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.8 | 57 | 10609 | 0.0754
N2XY | CU | XLPE | No | PVC | 5x10 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 20 | 829 | 1.83
N2XY | CU | XLPE | No | PVC | 5x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 22 | 1169 | 1.15
N2XY | CU | XLPE | No | PVC | 5x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.7 | 1.8 | 23 | 1188 | 1.15
N2XY | CU | XLPE | No | PVC | 5x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 27 | 1795 | 0.727
N2XY | CU | XLPE | No | PVC | 5x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 31 | 2363 | 0.524
N2XY | CU | XLPE | No | PVC | 5x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 2 | 35 | 3154 | 0.387
N2XY | CU | XLPE | No | PVC | 5x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 38 | 4146 | 0.268
N2XY | CU | XLPE | No | PVC | 5x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.3 | 42 | 5516 | 0.193
N2XY | CU | XLPE | No | PVC | 5x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.4 | 47 | 6805 | 0.153
N2X2Y | CU | XLPE | No | PE | 1x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 9 | 141 | 1.83
N2X2Y | CU | XLPE | No | PE | 1x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 10 | 200 | 1.15
N2X2Y | CU | XLPE | No | PE | 1x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 12 | 301 | 0.727
N2X2Y | CU | XLPE | No | PE | 1x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 13 | 397 | 0.524
N2X2Y | CU | XLPE | No | PE | 1x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 14 | 520 | 0.387
N2X2Y | CU | XLPE | No | PE | 1x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 16 | 725 | 0.268
N2X2Y | CU | XLPE | No | PE | 1x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 18 | 972 | 0.193
N2X2Y | CU | XLPE | No | PE | 1x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 20 | 1207 | 0.153
N2X2Y | CU | XLPE | No | PE | 1x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 22 | 1488 | 0.124
N2X2Y | CU | XLPE | No | PE | 1x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.7 | 1.8 | 26 | 2388 | 0.0991
N2X2Y | CU | XLPE | No | PE | 1x300 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 29 | 2964 | 0.0601
N2X2Y | CU | XLPE | No | PE | 1x400 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.9 | 32 | 3772 | 0.047
N2X2Y | CU | XLPE | No | PE | 1x500 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 2 | 36 | 4808 | 0.0366
N2X2Y | CU | XLPE | No | PE | 3x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 17 | 529 | 1.83
N2X2Y | CU | XLPE | No | PE | 3x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 19 | 741 | 1.15
N2X2Y | CU | XLPE | No | PE | 3x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 23 | 1122 | 0.727
N2X2Y | CU | XLPE | No | PE | 3x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 26 | 1473 | 0.524
N2X2Y | CU | XLPE | No | PE | 3x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.8 | 26 | 1729 | 0.387
N2X2Y | CU | XLPE | No | PE | 3x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 1.9 | 30 | 2414 | 0.268
N2X2Y | CU | XLPE | No | PE | 3x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 3210 | 0.193
N2X2Y | CU | XLPE | No | PE | 3x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.1 | 37 | 3962 | 0.153
N2X2Y | CU | XLPE | No | PE | 3x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.3 | 41 | 4906 | 0.124
N2X2Y | CU | XLPE | No | PE | 3x185 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 6047 | 0.0991
N2X2Y | CU | XLPE | No | PE | 3x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.6 | 51 | 7833 | 0.0754
N2X2Y | CU | XLPE | No | PE | 3x35+16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV/RE | 0.9/0.7 | 1.8 | 26 | 1652 | 0.524
N2X2Y | CU | XLPE | No | PE | 3x50+25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RMV | 1.0/0.9 | 1.8 | 29 | 2075 | 0.387
N2X2Y | CU | XLPE | No | PE | 3x70+35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/0.9 | 1.9 | 32 | 2828 | 0.268
N2X2Y | CU | XLPE | No | PE | 3x95+50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/1.0 | 2.1 | 37 | 3757 | 0.193
N2X2Y | CU | XLPE | No | PE | 3x120+70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2/1.1 | 2.2 | 40 | 4707 | 0.153
N2X2Y | CU | XLPE | No | PE | 3x150+70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4/1.1 | 2.3 | 45 | 5675 | 0.124
N2X2Y | CU | XLPE | No | PE | 3x185+95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.1 | 2.5 | 49 | 7071 | 0.0991
N2X2Y | CU | XLPE | No | PE | 3x240+120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7/1.2 | 2.7 | 56 | 9138 | 0.0754
N2X2Y | CU | XLPE | No | PE | 4x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 18 | 642 | 1.83
N2X2Y | CU | XLPE | No | PE | 4x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 21 | 910 | 1.15
N2X2Y | CU | XLPE | No | PE | 4x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 25 | 1391 | 0.727
N2X2Y | CU | XLPE | No | PE | 4x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 28 | 1834 | 0.524
N2X2Y | CU | XLPE | No | PE | 4x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.9 | 29 | 2255 | 0.387
N2X2Y | CU | XLPE | No | PE | 4x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 3158 | 0.268
N2X2Y | CU | XLPE | No | PE | 4x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 37 | 4200 | 0.193
N2X2Y | CU | XLPE | No | PE | 4x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.3 | 41 | 5259 | 0.153
N2X2Y | CU | XLPE | No | PE | 4x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.4 | 46 | 6439 | 0.124
N2X2Y | CU | XLPE | No | PE | 4x185 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.6 | 51 | 7967 | 0.0991
N2X2Y | CU | XLPE | No | PE | 4x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.8 | 57 | 10324 | 0.0754
N2X2Y | CU | XLPE | No | PE | 5x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 20 | 767 | 1.83
N2X2Y | CU | XLPE | No | PE | 5x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 22 | 1100 | 1.15
N2X2Y | CU | XLPE | No | PE | 5x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 27 | 1676 | 0.727
N2X2Y | CU | XLPE | No | PE | 5x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 31 | 2266 | 0.524
N2X2Y | CU | XLPE | No | PE | 5x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 2 | 33 | 2877 | 0.387
N2X2Y | CU | XLPE | No | PE | 5x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 38 | 3979 | 0.268
N2X2Y | CU | XLPE | No | PE | 5x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.3 | 42 | 5342 | 0.193
N2X2Y | CU | XLPE | No | PE | 5x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.4 | 47 | 6625 | 0.153
NA2XY | AL | XLPE | No | PE | 1x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.7 | 1.8 | 10 | 136 | 1.91
NA2XY | AL | XLPE | No | PE | 1x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 12 | 182 | 1.2
NA2XY | AL | XLPE | No | PE | 1x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 13 | 222 | 0.868
NA2XY | AL | XLPE | No | PE | 1x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 14 | 275 | 0.641
NA2XY | AL | XLPE | No | PE | 1x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 16 | 358 | 0.443
NA2XY | AL | XLPE | No | PE | 1x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 18 | 448 | 0.32
NA2XY | AL | XLPE | No | PE | 1x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 20 | 538 | 0.253
NA2XY | AL | XLPE | No | PE | 1x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 22 | 654 | 0.206
NA2XY | AL | XLPE | No | PE | 1x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 24 | 797 | 0.164
NA2XY | AL | XLPE | No | PE | 1x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.7 | 1.8 | 26 | 991 | 0.125
NA2XY | AL | XLPE | No | PE | 1x300 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 29 | 1194 | 0.1
NA2XY | AL | XLPE | No | PE | 1x400 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.9 | 32 | 1504 | 0.0778
NA2XY | AL | XLPE | No | PE | 1x500 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 2 | 36 | 1889 | 0.0605
NA2XY | AL | XLPE | No | PE | 3x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 19 | 513 | 1.91
NA2XY | AL | XLPE | No | PE | 3x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 22 | 703 | 1.2
NA2XY | AL | XLPE | No | PE | 3x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 25 | 868 | 0.868
NA2XY | AL | XLPE | No | PE | 3x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.8 | 26 | 955 | 0.641
NA2XY | AL | XLPE | No | PE | 3x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 1.9 | 30 | 1274 | 0.443
NA2XY | AL | XLPE | No | PE | 3x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 1584 | 0.32
NA2XY | AL | XLPE | No | PE | 3x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.1 | 39 | 1951 | 0.253
NA2XY | AL | XLPE | No | PE | 3x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.3 | 41 | 2354 | 0.206
NA2XY | AL | XLPE | No | PE | 3x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 2832 | 0.164
NA2XY | AL | XLPE | No | PE | 3x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.6 | 51 | 3597 | 0.125
NA2XY | AL | XLPE | No | PE | 3x25+16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9/0.7 | 1.8 | 23 | 770 | 1.2
NA2XY | AL | XLPE | No | PE | 3x35+16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9/0.7 | 1.8 | 25 | 940 | 0.868
NA2XY | AL | XLPE | No | PE | 3x50+25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RE | 1.0/0.9 | 1.8 | 29 | 1142 | 0.641
NA2XY | AL | XLPE | No | PE | 3x70+35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM/RE | 1.1/0.9 | 1.9 | 33 | 1509 | 0.443
NA2XY | AL | XLPE | No | PE | 3x95+50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/1.0 | 2.1 | 37 | 1859 | 0.32
NA2XY | AL | XLPE | No | PE | 3x120+70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2/1.1 | 2.2 | 40 | 2245 | 0.253
NA2XY | AL | XLPE | No | PE | 3x150+70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4/1.1 | 2.3 | 45 | 2720 | 0.206
NA2XY | AL | XLPE | No | PE | 3x185+95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.1 | 2.5 | 49 | 3310 | 0.164
NA2XY | AL | XLPE | No | PE | 3x240+120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7/1.2 | 2.7 | 56 | 4202 | 0.125
NA2XY | AL | XLPE | No | PE | 4x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.7 | 1.8 | 21 | 611 | 1.91
NA2XY | AL | XLPE | No | PE | 4x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 24 | 823 | 1.2
NA2XY | AL | XLPE | No | PE | 4x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 27 | 1015 | 0.868
NA2XY | AL | XLPE | No | PE | 4x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 0.9 | 1.8 | 26 | 960 | 0.868
NA2XY | AL | XLPE | No | PE | 4x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.9 | 32 | 1385 | 0.641
NA2XY | AL | XLPE | No | PE | 4x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1 | 1.9 | 27 | 1115 | 0.641
NA2XY | AL | XLPE | No | PE | 4x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.9 | 29 | 1192 | 0.641
NA2XY | AL | XLPE | No | PE | 4x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.1 | 2 | 32 | 1501 | 0.443
NA2XY | AL | XLPE | No | PE | 4x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.1 | 2.1 | 35 | 1901 | 0.32
NA2XY | AL | XLPE | No | PE | 4x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 37 | 2012 | 0.32
NA2XY | AL | XLPE | No | PE | 4x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.2 | 2.3 | 39 | 2376 | 0.253
NA2XY | AL | XLPE | No | PE | 4x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.4 | 2.4 | 43 | 2827 | 0.206
NA2XY | AL | XLPE | No | PE | 4x150 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.4 | 46 | 3007 | 0.206
NA2XY | AL | XLPE | No | PE | 4x185 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.6 | 2.6 | 48 | 3466 | 0.164
NA2XY | AL | XLPE | No | PE | 4x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SE | 1.7 | 2.8 | 54 | 4373 | 0.125
NA2XY | AL | XLPE | No | PE | 4x240 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.8 | 57 | 4648 | 0.125
NA2XY | AL | XLPE | No | PE | 5x16 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 23 | 688 | 1.91
NA2XY | AL | XLPE | No | PE | 5x25 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 26 | 955 | 1.2
NA2XY | AL | XLPE | No | PE | 5x35 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 29 | 1181 | 0.868
NA2XY | AL | XLPE | No | PE | 5x50 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 2 | 33 | 1543 | 0.641
NA2XY | AL | XLPE | No | PE | 5x70 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 38 | 2030 | 0.443
NA2XY | AL | XLPE | No | PE | 5x95 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.3 | 42 | 2604 | 0.32
NA2XY | AL | XLPE | No | PE | 5x120 | 0.6/1 | 4 | 250 | 90 | -5 | -35 | - 35 - +90 | HD 308 S2 | black | IEC 60332-1-2 | Eca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.4 | 47 | 3159 | 0.253
NA2X2Y | AL | XLPE | No | PE | 1x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 10 | 104 | 1.91
NA2X2Y | AL | XLPE | No | PE | 1x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 12 | 144 | 1.2
NA2X2Y | AL | XLPE | No | PE | 1x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 13 | 179 | 0.868
NA2X2Y | AL | XLPE | No | PE | 1x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1 | 1.8 | 14 | 232 | 0.641
NA2X2Y | AL | XLPE | No | PE | 1x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 16 | 309 | 0.443
NA2X2Y | AL | XLPE | No | PE | 1x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.1 | 1.8 | 18 | 394 | 0.32
NA2X2Y | AL | XLPE | No | PE | 1x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.2 | 1.8 | 20 | 479 | 0.253
NA2X2Y | AL | XLPE | No | PE | 1x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.4 | 1.8 | 22 | 587 | 0.206
NA2X2Y | AL | XLPE | No | PE | 1x185 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.6 | 1.8 | 24 | 722 | 0.164
NA2X2Y | AL | XLPE | No | PE | 1x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.7 | 1.8 | 26 | 908 | 0.125
NA2X2Y | AL | XLPE | No | PE | 1x300 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 1.8 | 1.8 | 29 | 1102 | 0.1
NA2X2Y | AL | XLPE | No | PE | 1x400 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2 | 1.9 | 32 | 1398 | 0.0078
NA2X2Y | AL | XLPE | No | PE | 1x500 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 2.2 | 2 | 36 | 1763 | 0.065
NA2X2Y | AL | XLPE | No | PE | 3x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 19 | 454 | 1.91
NA2X2Y | AL | XLPE | No | PE | 3x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 22 | 634 | 1.2
NA2X2Y | AL | XLPE | No | PE | 3x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9 | 1.8 | 25 | 788 | 0.868
NA2X2Y | AL | XLPE | No | PE | 3x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.8 | 26 | 870 | 0.641
NA2X2Y | AL | XLPE | No | PE | 3x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 1.9 | 30 | 1170 | 0.443
NA2X2Y | AL | XLPE | No | PE | 3x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 1463 | 0.32
NA2X2Y | AL | XLPE | No | PE | 3x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.1 | 39 | 1802 | 0.253
NA2X2Y | AL | XLPE | No | PE | 3x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.3 | 41 | 2184 | 0.206
NA2X2Y | AL | XLPE | No | PE | 3x185 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.4 | 45 | 2647 | 0.164
NA2X2Y | AL | XLPE | No | PE | 3x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.6 | 51 | 3362 | 0.125
NA2X2Y | AL | XLPE | No | PE | 3x35+16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.9/0.7 | 1.8 | 25 | 855 | 0.868
NA2X2Y | AL | XLPE | No | PE | 3x70+35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/0.9 | 1.9 | 32 | 2828 | 0.268
NA2X2Y | AL | XLPE | No | PE | 3x95+50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1/1.0 | 2.1 | 37 | 3757 | 0.193
NA2X2Y | AL | XLPE | No | PE | 3x120+70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2/1.1 | 2.2 | 40 | 4707 | 0.153
NA2X2Y | AL | XLPE | No | PE | 3x150+70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4/1.1 | 2.3 | 45 | 5675 | 0.124
NA2X2Y | AL | XLPE | No | PE | 3x185+95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6/1.1 | 2.5 | 49 | 7071 | 0.0991
NA2X2Y | AL | XLPE | No | PE | 3x240+120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7/1.2 | 2.7 | 56 | 9138 | 0.0754
NA2X2Y | AL | XLPE | No | PE | 4x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 18 | 642 | 1.83
NA2X2Y | AL | XLPE | No | PE | 4x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 21 | 910 | 1.15
NA2X2Y | AL | XLPE | No | PE | 4x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 25 | 1391 | 0.727
NA2X2Y | AL | XLPE | No | PE | 4x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 28 | 1834 | 0.524
NA2X2Y | AL | XLPE | No | PE | 4x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 1.9 | 29 | 2255 | 0.387
NA2X2Y | AL | XLPE | No | PE | 4x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2 | 33 | 3158 | 0.268
NA2X2Y | AL | XLPE | No | PE | 4x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 37 | 4200 | 0.193
NA2X2Y | AL | XLPE | No | PE | 4x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.3 | 41 | 5259 | 0.153
NA2X2Y | AL | XLPE | No | PE | 4x150 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.4 | 2.4 | 46 | 6439 | 0.124
NA2X2Y | AL | XLPE | No | PE | 4x185 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.6 | 2.6 | 51 | 7967 | 0.0991
NA2X2Y | AL | XLPE | No | PE | 4x240 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.7 | 2.8 | 57 | 10324 | 0.0754
NA2X2Y | AL | XLPE | No | PE | 5x10 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 20 | 767 | 1.83
NA2X2Y | AL | XLPE | No | PE | 5x16 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RE | 0.7 | 1.8 | 22 | 1100 | 1.15
NA2X2Y | AL | XLPE | No | PE | 5x25 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 27 | 1676 | 0.727
NA2X2Y | AL | XLPE | No | PE | 5x35 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | RMV | 0.9 | 1.8 | 31 | 2266 | 0.524
NA2X2Y | AL | XLPE | No | PE | 5x50 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1 | 2 | 33 | 2877 | 0.387
NA2X2Y | AL | XLPE | No | PE | 5x70 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.1 | 38 | 3979 | 0.268
NA2X2Y | AL | XLPE | No | PE | 5x95 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.1 | 2.3 | 42 | 5342 | 0.193
NA2X2Y | AL | XLPE | No | PE | 5x120 | 0.6/1 | 4 | 250 | 90 | -20 | -35 | - 35 - +90 | HD 308 S2 | black | no | Fca | cable drums | yes/yes | 15xD (Single core); 12xD (Multi core) | SM | 1.2 | 2.4 | 47 | 6625 | 0.153