{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["NY2Y"],"read":"whole","date_system":"1900"}

{"sheet":"NY2Y","index":0,"n_rows":55,"n_cols":9,"rows_kept":55}
["NY2Y"]
["Kategorien:","Niederspannungskabel"]
["Artikelnummer:","NY2Y-low-voltage-cables"]
[]
["ANWENDUNG"]
["Das NY2Y ist ein besonders widerstandsfähiges Niederspannungskabel für die feste Verlegung unter hohen mechanischen Anforderungen – ob im Erdreich, im Wasser oder in industrieller Umgebung. Dank seiner Materialkombination ist es für vielfältige Einsatzbedingungen bestens geeignet."]
[]
["TECHNISCHE DATEN"]
["Biegeradius (min.) (mm)","15/12xD mm"]
["Colour of insulation","HD 308 S2"]
["Colour of sheath","black"]
["CPR-Klasse","Fca"]
["CUScreen","No"]
["Flammhemmend","no"]
["Isolierung","PVC"]
["Kurzschlusstemperatur (max.) (°C)","≤ 300 mm2: +160, > 300 mm2: +140 °C"]
["Leiter","CU"]
["Leitertemperatur (max.) (°C)","70 °C"]
["Mantel","PE"]
["Minimale Lagertemperatur (°C)","-35 °C"]
["Minimale Verlegetemperatur (°C)","-5 °C"]
["Nennspannung (kV)","0.6/1 kV"]
["Prüfspannung (kV)","4 kV"]
["RoHS/REACH","yes/yes"]
["Temperaturbereich (°C)","-35-+70 °C"]
["Verpackung","cable drums"]
[]
["KONFIGURATIONEN"]
["Querschnitt","Leiter","DI [mm]","RI [Ohm/km]","Wi [mm]","Wm [mm]","Rbv [mm]","Ø [mm]","G [kg/km]"]
["1x10","Cu","~6,4","1,83","1","1,8","15/12xD","10","157"]
["1x16","Cu","~7,4","1,15","1","1,8","15/12xD","11","219"]
["1x25","Cu","~8,4","0,727","1,2","1,8","15/12xD","12","329"]
["1x35","Cu","~10,4","0,524","1,2","1,8","15/12xD","14","429"]
["1x50","Cu","~11,4","0,387","1,4","1,8","15/12xD","15","565"]
["1x70","Cu","~13,4","0,268","1,4","1,8","15/12xD","17","772"]
["1x95","Cu","~15,4","0,193","1,6","1,8","15/12xD","19","1042"]
["1x120","Cu","~16,4","0,153","1,6","1,8","15/12xD","20","1278"]
["1x150","Cu","~18,4","0,124","1,8","1,8","15/12xD","22","1571"]
["1x185","Cu","~21,4","0,0991","2","1,8","15/12xD","25","1947"]
["1x240","Cu","~23,4","0,0754","2,2","1,8","15/12xD","27","2514"]
["1x300","Cu","~26,2","0,0601","2,4","1,9","15/12xD","30","3130"]
["1x400","Cu","~30","0,047","2,6","2","15/12xD","34","3972"]
["1x500","Cu","~32,8","0,0366","2,8","2,1","15/12xD","37","5043"]
["3x10","Cu","~14,4","1,83","1","1,8","15/12xD","18","589"]
["3x16","Cu","~16,4","1,15","1","1,8","15/12xD","20","810"]
["3x25","Cu","~20,4","0,727","1,2","1,8","15/12xD","24","1227"]
["3x35","Cu","~21,4","0,524","1,2","1,8","15/12xD","25","1464"]
["3x50","Cu","~24,4","0,387","1,4","1,8","15/12xD","28","1887"]
["3x70","Cu","~27","0,268","1,4","2","15/12xD","31","2584"]
["3x95","Cu","~31,8","0,193","1,6","2,1","15/12xD","36","3448"]
["3x120","Cu","~33,6","0,153","1,6","2,2","15/12xD","38","4199"]
["3x150","Cu","~38,4","0,124","1,8","2,3","15/12xD","43","5178"]
["3x185","Cu","~42","0,0991","2","2,5","15/12xD","47","6381"]
["3x240","Cu","~47,6","0,0754","2,2","2,7","15/12xD","53","8264"]
["3x35+16","Cu","~23,4","0,524","1.2/1.0","1,8","15/12xD","27","1698"]