{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["N2X2Y"],"read":"whole","date_system":"1900"}

{"sheet":"N2X2Y","index":0,"n_rows":80,"n_cols":9,"rows_kept":80}
["N2X2Y"]
["Categories:","Niederspannungskabel"]
["SKU:","N2X2Y-low-voltage-cables"]
[]
["APPLICATION"]
["The N2X2Y cable is an XLPE-insulated low-voltage cable with an HDPE sheath, developed for fixed installations under demanding conditions. It stands out for its high thermal endurance and is ideally suited for use in power distribution systems with increased safety requirements."]
[]
["TECHNICAL DATA"]
["Bending radius (mm)","15/12xD mm"]
["Colour of insulation","HD 308 S2"]
["Colour of sheath","black"]
["Conductor","CU"]
["CPR class","Fca"]
["CUScreen","No"]
["Insulation","XLPE"]
["Maximal operating conductor temperature (°C)","90 °C"]
["Maximal short-circuit temperature (°C)","250 °C"]
["Minimal storage temperature (°C)","-35 °C"]
["Minimal temperature for laying (°C)","-20 °C"]
["Operating temperature range (°C)","-35-+90 °C"]
["Packaging","cable drums"]
["Rated voltage (kV)","0.6/1 kV"]
["RoHS/REACH","yes/yes"]
["Self-extinguishing of single cable","no"]
["Sheath","PE"]
["Test voltage (kV)","4 kV"]
[]
["CONFIGURATIONS"]
["Cross-section","Cond.","DI [mm]","RI [Ohm/km]","Wi [mm]","Wm [mm]","Rbv [mm]","Ø [mm]","G [kg/km]"]
["1x10","Cu","~5.4","1.83","0.7","1.8","15/12xD","9","141"]
["1x16","Cu","~6.4","1.15","0.7","1.8","15/12xD","10","200"]
["1x25","Cu","~8.4","0.727","0.9","1.8","15/12xD","12","301"]
["1x35","Cu","~9.4","0.524","0.9","1.8","15/12xD","13","397"]
["1x50","Cu","~10.4","0.387","1","1.8","15/12xD","14","520"]
["1x70","Cu","~12.4","0.268","1.1","1.8","15/12xD","16","725"]
["1x95","Cu","~14.4","0.193","1.1","1.8","15/12xD","18","972"]
["1x120","Cu","~16.4","0.153","1.2","1.8","15/12xD","20","1207"]
["1x150","Cu","~18.4","0.124","1.4","1.8","15/12xD","22","1488"]
["1x240","Cu","~22.4","0.0991","1.7","1.8","15/12xD","26","2388"]
["1x300","Cu","~25.4","0.0601","1.8","1.8","15/12xD","29","2964"]
["1x400","Cu","~28.2","0.047","2","1.9","15/12xD","32","3772"]
["1x500","Cu","~32","0.0366","2.2","2","15/12xD","36","4808"]
["3x10","Cu","~13.4","1.83","0.7","1.8","15/12xD","17","529"]
["3x16","Cu","~15.4","1.15","0.7","1.8","15/12xD","19","741"]
["3x25","Cu","~19.4","0.727","0.9","1.8","15/12xD","23","1122"]
["3x35","Cu","~22.4","0.524","0.9","1.8","15/12xD","26","1473"]
["3x50","Cu","~22.4","0.387","1","1.8","15/12xD","26","1729"]
["3x70","Cu","~26.2","0.268","1.1","1.9","15/12xD","30","2414"]
["3x95","Cu","~29","0.193","1.1","2","15/12xD","33","3210"]
["3x120","Cu","~32.8","0.153","1.2","2.1","15/12xD","37","3962"]
["3x150","Cu","~36.4","0.124","1.4","2.3","15/12xD","41","4906"]
["3x185","Cu","~40.2","0.0991","1.6","2.4","15/12xD","45","6047"]
["3x240","Cu","~45.8","0.0754","1.7","2.6","15/12xD","51","7833"]
["3x35+16","Cu","~22.4","0.524","0.9/0.7","1.8","15/12xD","26","1652"]
["3x50+25","Cu","~25.4","0.387","1.0/0.9","1.8","15/12xD","29","2075"]
["3x70+35","Cu","~28.2","0.268","1.1/0.9","1.9","15/12xD","32","2828"]
["3x95+50","Cu","~32.8","0.193","1.1/1.0","2.1","15/12xD","37","3757"]
["3x120+70","Cu","~35.6","0.153","1.2/1.1","2.2","15/12xD","40","4707"]
["3x150+70","Cu","~40.4","0.124","1.4/1.1","2.3","15/12xD","45","5675"]
["3x185+95","Cu","~44","0.0991","1.6/1.1","2.5","15/12xD","49","7071"]
["3x240+120","Cu","~50.6","0.0754","1.7/1.2","2.7","15/12xD","56","9138"]
["4x10","Cu","~14.4","1.83","0.7","1.8","15/12xD","18","642"]
["4x16","Cu","~17.4","1.15","0.7","1.8","15/12xD","21","910"]
["4x25","Cu","~21.4","0.727","0.9","1.8","15/12xD","25","1391"]
["4x35","Cu","~24.4","0.524","0.9","1.8","15/12xD","28","1834"]
["4x50","Cu","~25.2","0.387","1","1.9","15/12xD","29","2255"]
["4x70","Cu","~29","0.268","1.1","2","15/12xD","33","3158"]
["4x95","Cu","~32.8","0.193","1.1","2.1","15/12xD","37","4200"]
["4x120","Cu","~36.4","0.153","1.2","2.3","15/12xD","41","5259"]
["4x150","Cu","~41.2","0.124","1.4","2.4","15/12xD","46","6439"]
["4x185","Cu","~45.8","0.0991","1.6","2.6","15/12xD","51","7967"]
["4x240","Cu","~51.4","0.0754","1.7","2.8","15/12xD","57","10324"]
["5x10","Cu","~16.4","1.83","0.7","1.8","15/12xD","20","767"]
["5x16","Cu","~18.4","1.15","0.7","1.8","15/12xD","22","1100"]
["5x25","Cu","~23.4","0.727","0.9","1.8","15/12xD","27","1676"]
["5x35","Cu","~27.4","0.524","0.9","1.8","15/12xD","31","2266"]
["5x50","Cu","~29","0.387","1","2","15/12xD","33","2877"]
["5x70","Cu","~33.8","0.268","1.1","2.1","15/12xD","38","3979"]
["5x95","Cu","~37.4","0.193","1.1","2.3","15/12xD","42","5342"]
["5x120","Cu","~42.2","0.153","1.2","2.4","15/12xD","47","6625"]