## Sheet 1
[22 empty] | LF | LD mm | ID mm | DI mm | MWD mm | AD mm | BR | G kg | RI Ohm |  |  |  |  | BK |  |  |  | SBL 30 |  | SBE 20
Part Number | Conductor | Insulation | Conductive tape below screen | Copper wire screen and tape | Non conducting tape above screen | Al Foil | Sheath | Querschnitt | Rated voltage | Test voltage | Maximal operating conductor temperature | Maximal short-circuit temperature | Operating temperature range | Minimal storage temperature | Minimal temperature for laying | Colour of insulation | Colour of sheath | Flame retardant | CPR class | Packaging | CE-Conformity | Leiterform | Leiterdurchmesser ca. | Isolierwanddicke NWD | Durchmesser über Isolierung ca. | Manteldicke Kleinstwert | Aussendurchmesser ca. | Biegeradius | Gewicht ca. | RI Ohm/km 20Grad | Capacitance (approx.) | Inductance, trefoil (approx.) | Inductance in air, flat (approx.) 1 | Inductance in ground, flat (approx.) 1 | Bemessungs-Kurzschlußstrom 1 s | Screen shortcircuit current | Heating time constant, trefoil* | Heating time constant, flat* | Strombelastbarkeit in Luft 30 Grad | Current ratings in air, flat* | Strombelastbarkeit in Erde 20 Grad | Current ratings in ground, flat*
Units | [7 empty] | mm2 | kV | kV | °C | °C | °C | °C | °C | [7 empty] | mm | mm | mm | mm | mm | mm | kg/km | Ω/km | μF/km | mH/km | mH/km | mH/km | kA | kA | s | s | A | A | A | A
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x35/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 7.2 | 3.4 | 15.3 | 2.1 | 24 | 360 | 904 | 0.524 | 0.22 | 0.43 |  | 0.73 | 5 | 3.2 | 275 | 198 | 197 | 235 | 187 | 212
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-3 | Eca | wooden or metal drums | yes | RM | 8.2 | 3.4 | 16.3 | 2.1 | 26 | 390 | 1039 | 0.387 | 0.24 | 0.42 |  | 0.71 | 7.1 | 3.2 | 387 | 281 | 238 | 282 | 220 | 249
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-4 | Eca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 27 | 405 | 1271 | 0.268 | 0.28 | 0.39 |  | 0.67 | 10 | 3.2 | 503 | 368 | 294 | 350 | 268 | 302
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-5 | Eca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 29 | 435 | 1530 | 0.193 | 0.3 | 0.38 |  | 0.65 | 13.6 | 3.2 | 630 | 465 | 358 | 426 | 320 | 359
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-6 | Eca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 30 | 450 | 1809 | 0.153 | 0.34 | 0.36 |  | 0.62 | 17.1 | 3.2 | 763 | 569 | 413 | 491 | 363 | 405
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-7 | Eca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 32 | 480 | 2158 | 0.124 | 0.36 | 0.35 |  | 0.6 | 21.4 | 5 | 948 | 743 | 468 | 549 | 405 | 442
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-8 | Eca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 33 | 495 | 2524 | 0.099 | 0.4 | 0.34 |  | 0.58 | 26.4 | 5 | 1125 | 897 | 535 | 625 | 456 | 493
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-9 | Eca | wooden or metal drums | yes | RM | 18.3 | 3.4 | 26.4 | 2.1 | 36 | 540 | 3117 | 0.075 | 0.44 | 0.32 |  | 0.55 | 34.3 | 5 | 1370 | 1135 | 631 | 731 | 526 | 563
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-10 | Eca | wooden or metal drums | yes | RM | 20.7 | 3.4 | 28.8 | 2.1 | 38 | 570 | 3786 | 0.06 | 0.49 | 0.31 |  | 0.53 | 42.9 | 5 | 1636 | 1377 | 722 | 831 | 591 | 626
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-11 | Eca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 41 | 615 | 4750 | 0.047 | 0.54 | 0.29 |  | 0.5 | 57.2 | 7 | 2352 | 2133 | 827 | 920 | 662 | 675
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –25 | -5 | uncoloured | red or black | EN 60 332-1-12 | Eca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 44 | 660 | 5786 | 0.037 | 0.61 | 0.28 |  | 0.48 | 71.4 | 7 | 2917 | 2727 | 949 | 1043 | 744 | 748
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x35/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 7.2 | 3.4 | 15.3 | 2.1 | 24 | 360 | 803 | 0.524 | 0.22 | 0.43 |  | 0.73 | 5 | 3.2 | 267 | 190 | 197 | 235 | 187 | 212
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 3.4 | 16.3 | 2.1 | 25 | 375 | 928 | 0.387 | 0.24 | 0.42 |  | 0.71 | 7.1 | 3.2 | 375 | 269 | 238 | 282 | 220 | 249
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 26 | 390 | 1154 | 0.268 | 0.28 | 0.39 |  | 0.67 | 10 | 3.2 | 488 | 352 | 294 | 350 | 268 | 302
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 28 | 420 | 1410 | 0.193 | 0.3 | 0.38 |  | 0.65 | 13.6 | 3.2 | 611 | 446 | 358 | 426 | 320 | 359
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 30 | 450 | 1682 | 0.153 | 0.34 | 0.36 |  | 0.62 | 17.1 | 3.2 | 742 | 545 | 413 | 491 | 363 | 405
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 31 | 465 | 2025 | 0.124 | 0.36 | 0.35 |  | 0.6 | 21.4 | 5 | 917 | 709 | 468 | 549 | 405 | 442
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 32 | 480 | 2383 | 0.099 | 0.4 | 0.34 |  | 0.58 | 26.4 | 5 | 1089 | 861 | 535 | 625 | 456 | 493
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 3.4 | 26.4 | 2.1 | 35 | 525 | 2965 | 0.075 | 0.44 | 0.32 |  | 0.55 | 34.3 | 5 | 1318 | 1073 | 631 | 731 | 526 | 563
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 3.4 | 28.8 | 2.1 | 37 | 555 | 3624 | 0.06 | 0.49 | 0.31 |  | 0.53 | 42.9 | 5 | 1582 | 1309 | 722 | 831 | 591 | 626
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 40 | 600 | 4574 | 0.047 | 0.54 | 0.29 |  | 0.5 | 57.2 | 7 | 2279 | 2036 | 827 | 920 | 662 | 675
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 43 | 645 | 5597 | 0.037 | 0.61 | 0.28 |  | 0.48 | 71.4 | 7 | 2765 | 2538 | 949 | 1043 | 744 | 748
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 3.4 | 16.3 | 2.1 | 26 | 375 | 928 | 0.387 | 0.24 | 0.41 |  | 0.71 | 7.1 | 3.2 | 385 | 275 | 238 | 282 | 220 | 249
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 26 | 390 | 1155 | 0.268 | 0.28 | 0.39 |  | 0.67 | 10 | 3.2 | 491 | 353 | 294 | 350 | 268 | 302
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 28 | 420 | 1410 | 0.193 | 0.3 | 0.37 |  | 0.65 | 13.6 | 3.2 | 618 | 450 | 358 | 426 | 320 | 359
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 30 | 450 | 1683 | 0.153 | 0.34 | 0.36 |  | 0.62 | 17.1 | 3.2 | 744 | 550 | 413 | 491 | 363 | 405
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 31 | 465 | 2052 | 0.124 | 0.36 | 0.34 |  | 0.59 | 21.4 | 5 | 927 | 719 | 468 | 549 | 405 | 442
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 32 | 480 | 2384 | 0.099 | 0.4 | 0.33 |  | 0.58 | 26.4 | 5 | 1094 | 866 | 535 | 625 | 456 | 493
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 3.4 | 26.4 | 2.1 | 35 | 525 | 2964 | 0.075 | 0.44 | 0.32 |  | 0.55 | 34.3 | 5 | 1327 | 1082 | 631 | 731 | 526 | 563
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 3.4 | 28.8 | 2.1 | 37 | 555 | 3624 | 0.06 | 0.49 | 0.31 |  | 0.53 | 42.9 | 5 | 1582 | 1309 | 722 | 831 | 591 | 626
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 40 | 600 | 4575 | 0.047 | 0.54 | 0.29 |  | 0.5 | 57.2 | 7 | 2279 | 2061 | 827 | 920 | 662 | 675
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 43 | 645 | 5598 | 0.037 | 0.61 | 0.28 |  | 0.48 | 71.4 | 7 | 2803 | 2614 | 949 | 1043 | 744 | 748
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 3.4 | 16.3 | 2.1 | 26 | 520 | 1010 | 0.387 | 0.24 | 0.41 |  | 0.7 | 7.1 | 3.2 | 383 | 273 | 238 | 282 | 220 | 249
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 28 | 560 | 1238 | 0.268 | 0.28 | 0.39 |  | 0.67 | 10 | 3.2 | 490 | 353 | 294 | 350 | 268 | 302
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 29 | 580 | 1495 | 0.193 | 0.3 | 0.37 |  | 0.65 | 13.6 | 3.2 | 618 | 450 | 358 | 426 | 320 | 359
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 31 | 620 | 1773 | 0.153 | 0.34 | 0.36 |  | 0.62 | 17.1 | 3.2 | 742 | 545 | 413 | 491 | 363 | 405
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 32 | 640 | 2119 | 0.124 | 0.36 | 0.34 |  | 0.59 | 21.4 | 5 | 927 | 719 | 468 | 549 | 405 | 442
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 34 | 680 | 2483 | 0.099 | 0.4 | 0.33 |  | 0.58 | 26.4 | 5 | 1094 | 866 | 535 | 625 | 456 | 493
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 3.4 | 26.4 | 2.1 | 36 | 720 | 3073 | 0.075 | 0.44 | 0.32 |  | 0.55 | 34.3 | 5 | 1335 | 1091 | 631 | 731 | 526 | 563
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 3.4 | 28.8 | 2.1 | 39 | 780 | 3737 | 0.06 | 0.48 | 0.31 |  | 0.54 | 42.9 | 5 | 1595 | 1336 | 722 | 831 | 591 | 626
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 42 | 840 | 4697 | 0.047 | 0.54 | 0.29 |  | 0.5 | 57.2 | 7 | 2303 | 2036 | 827 | 920 | 662 | 675
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | –35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 44 | 880 | 5729 | 0.037 | 0.61 | 0.28 |  | 0.48 | 71.4 | 7 | 2803 | 2538 | 949 | 1043 | 744 | 748
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x35/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 7.2 | 3.4 | 15.3 | 2.1 | 24 | 360 | 668 | 0.868 | 0.22 | 0.44 | 0.61 | 0.74 | 3.3 | 3.2 | 197 | 140 | 153 | 182 | 145 | 165
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-3 | Eca | wooden or metal drums | yes | RM | 8.3 | 3.4 | 16.4 | 2.1 | 25 | 375 | 734 | 0.641 | 0.25 | 0.42 | 0.6 | 0.71 | 4.7 | 3.2 | 278 | 198 | 183 | 219 | 171 | 194
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-4 | Eca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 27 | 405 | 824 | 0.443 | 0.28 | 0.39 | 0.57 | 0.68 | 6.6 | 3.2 | 363 | 260 | 228 | 273 | 208 | 236
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-5 | Eca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 28 | 420 | 932 | 0.32 | 0.31 | 0.37 | 0.54 | 0.65 | 9 | 3.2 | 452 | 325 | 278 | 333 | 248 | 281
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-6 | Eca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 30 | 450 | 1036 | 0.253 | 0.34 | 0.36 | 0.53 | 0.62 | 11.3 | 3.2 | 541 | 393 | 321 | 384 | 283 | 318
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-7 | Eca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 31 | 465 | 1222 | 0.206 | 0.37 | 0.34 | 0.51 | 0.59 | 14.2 | 5 | 667 | 501 | 364 | 432 | 315 | 350
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x185/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-8 | Eca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 33 | 495 | 1283 | 0.164 | 0.4 | 0.34 | 0.51 | 0.59 | 17.5 | 3.2 | 762 | 563 | 418 | 496 | 357 | 394
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-9 | Eca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 33 | 495 | 1372 | 0.164 | 0.41 | 0.33 | 0.49 | 0.57 | 17.5 | 5 | 771 | 590 | 418 | 496 | 357 | 394
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-10 | Eca | wooden or metal drums | yes | RM | 18.1 | 3.4 | 26.2 | 2.1 | 35 | 525 | 1579 | 0.125 | 0.44 | 0.32 | 0.48 | 0.55 | 22.7 | 5 | 955 | 745 | 494 | 583 | 413 | 452
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-11 | Eca | wooden or metal drums | yes | RM | 20.2 | 3.4 | 28.3 | 2.1 | 38 | 570 | 1834 | 0.1 | 0.48 | 0.31 | 0.47 | 0.54 | 28.4 | 5 | 1146 | 907 | 568 | 666 | 466 | 506
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-12 | Eca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 40 | 600 | 2263 | 0.0778 | 0.54 | 0.29 | 0.45 | 0.5 | 37.8 | 7 | 1549 | 1315 | 660 | 755 | 529 | 558
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-13 | Eca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 43 | 645 | 2643 | 0.0605 | 0.62 | 0.28 | 0.43 | 0.48 | 47.3 | 7 | 1823 | 1575 | 767 | 868 | 602 | 627
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x630/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-14 | Eca | wooden or metal drums | yes | RM | 29.9 | 3.4 | 38 | 2.1 | 47 | 705 | 3120 | 0.0469 | 0.67 | 0.27 | 0.42 | 0.46 | 59.6 | 7 | 2237 | 2000 | 840 | 889 | 681 | 661
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x800/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-15 | Eca | wooden or metal drums | yes | RM | 34.2 | 3.4 | 42.3 | 2.4 | 51 | 765 | 3760 | 0.0367 | 0.76 | 0.26 | 0.41 | 0.44 | 75.6 | 7 | 2800 | 2546 | 953 | 1000 | 754 | 725
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x1000/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-16 | Eca | wooden or metal drums | yes | RM | 38.1 | 3.4 | 46.2 | 2.4 | 57 | 855 | 4724 | 0.0291 | 0.84 | 0.25 | 0.4 | 0.42 | 94 | 7 | 3505 | 3157 | 1187 | 1270 | 852 | 842
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x35/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 7.2 | 3.4 | 15.3 | 2.1 | 23 | 345 | 563 | 0.868 | 0.22 | 0.43 | 0.61 | 0.73 | 3.3 | 3.2 | 194 | 136 | 153 | 182 | 145 | 165
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 3.4 | 16.4 | 2.1 | 25 | 375 | 624 | 0.641 | 0.25 | 0.42 | 0.6 | 0.71 | 4.7 | 3.2 | 270 | 191 | 183 | 219 | 171 | 194
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 26 | 390 | 707 | 0.443 | 0.28 | 0.39 | 0.56 | 0.68 | 6.6 | 3.2 | 353 | 249 | 228 | 273 | 208 | 236
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 28 | 420 | 808 | 0.32 | 0.31 | 0.38 | 0.55 | 0.65 | 9 | 3.2 | 440 | 314 | 278 | 333 | 248 | 281
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 29 | 435 | 905 | 0.253 | 0.34 | 0.36 | 0.53 | 0.63 | 11.3 | 3.2 | 528 | 379 | 321 | 384 | 283 | 318
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 30 | 450 | 1085 | 0.206 | 0.36 | 0.35 | 0.51 | 0.6 | 14.2 | 5 | 655 | 486 | 364 | 432 | 315 | 350
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 32 | 480 | 1226 | 0.164 | 0.4 | 0.33 | 0.5 | 0.58 | 17.5 | 5 | 760 | 574 | 418 | 496 | 357 | 394
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 3.4 | 26.2 | 2.1 | 34 | 510 | 1423 | 0.125 | 0.44 | 0.32 | 0.48 | 0.55 | 22.7 | 5 | 928 | 710 | 494 | 583 | 413 | 452
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 3.4 | 28.3 | 2.1 | 37 | 555 | 1666 | 0.1 | 0.48 | 0.31 | 0.47 | 0.54 | 28.4 | 5 | 1098 | 859 | 568 | 666 | 466 | 506
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 40 | 600 | 2082 | 0.0778 | 0.54 | 0.3 | 0.45 | 0.5 | 37.8 | 7 | 1496 | 1262 | 660 | 755 | 529 | 558
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 43 | 645 | 2447 | 0.0605 | 0.61 | 0.28 | 0.43 | 0.48 | 47.3 | 7 | 1773 | 1508 | 767 | 868 | 602 | 627
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 3.4 | 38 | 2.1 | 46 | 690 | 2909 | 0.0469 | 0.66 | 0.27 | 0.42 | 0.46 | 59.6 | 7 | 2158 | 1895 | 855 | 913 | 685 | 668
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 3.4 | 42.3 | 2.4 | 51 | 765 | 3520 | 0.0367 | 0.76 | 0.26 | 0.41 | 0.44 | 75.6 | 7 | 2716 | 2461 | 968 | 1017 | 764 | 731
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 3.4 | 46.2 | 2.4 | 57 | 855 | 4422 | 0.0291 | 0.84 | 0.25 | 0.4 | 0.42 | 94 | 7 | 3505 | 3157 | 1187 | 1270 | 852 | 842
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 3.4 | 16.4 | 2.1 | 25 | 375 | 625 | 0.641 | 0.24 | 0.41 | 0.59 | 0.71 | 4.7 | 3.2 | 277 | 195 | 183 | 219 | 171 | 194
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 26 | 390 | 707 | 0.443 | 0.28 | 0.39 | 0.56 | 0.68 | 6.6 | 3.2 | 353 | 249 | 228 | 273 | 208 | 236
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 28 | 420 | 808 | 0.32 | 0.31 | 0.37 | 0.55 | 0.65 | 9 | 3.2 | 443 | 316 | 278 | 333 | 248 | 281
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 29 | 435 | 909 | 0.253 | 0.34 | 0.36 | 0.53 | 0.63 | 11.3 | 3.2 | 529 | 379 | 321 | 384 | 283 | 318
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 30 | 450 | 1089 | 0.206 | 0.36 | 0.35 | 0.51 | 0.6 | 14.2 | 5 | 655 | 486 | 364 | 432 | 315 | 350
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 32 | 480 | 1232 | 0.164 | 0.4 | 0.33 | 0.5 | 0.58 | 17.5 | 5 | 760 | 574 | 418 | 496 | 357 | 394
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 3.4 | 26.2 | 2.1 | 34 | 510 | 1427 | 0.125 | 0.44 | 0.32 | 0.48 | 0.56 | 22.7 | 5 | 924 | 710 | 494 | 583 | 413 | 452
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 3.4 | 28.3 | 2.1 | 37 | 555 | 1666 | 0.1 | 0.48 | 0.31 | 0.47 | 0.54 | 28.4 | 5 | 1110 | 865 | 568 | 666 | 466 | 506
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 40 | 600 | 2089 | 0.0778 | 0.54 | 0.29 | 0.45 | 0.5 | 37.8 | 7 | 1506 | 1252 | 660 | 755 | 529 | 558
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 43 | 645 | 2456 | 0.0605 | 0.61 | 0.28 | 0.43 | 0.48 | 47.3 | 7 | 1773 | 1508 | 767 | 868 | 602 | 627
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 3.4 | 38 | 2.1 | 46 | 690 | 2909 | 0.0469 | 0.67 | 0.27 | 0.42 | 0.46 | 59.6 | 7 | 2158 | 1921 | 855 | 907 | 688 | 664
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 3.4 | 42.3 | 2.4 | 51 | 765 | 3521 | 0.0367 | 0.76 | 0.26 | 0.41 | 0.44 | 75.6 | 7 | 2716 | 2461 | 968 | 1017 | 764 | 731
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 3.4 | 46.2 | 2.4 | 55 | 825 | 4195 | 0.0291 | 0.84 | 0.25 | 0.4 | 0.42 | 94 | 7 | 3505 | 3157 | 1187 | 1270 | 852 | 842
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x35/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 7.2 | 3.4 | 15.3 | 2.1 | 25 | 500 | 643 | 0.868 | 0.22 | 0.44 | 0.61 | 0.74 | 3.3 | 3.2 | 191 | 135 | 160 | 190 | 145 | 165
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 3.4 | 16.4 | 2.1 | 26 | 520 | 712 | 0.641 | 0.25 | 0.42 | 0.59 | 0.71 | 4.7 | 3.2 | 273 | 193 | 183 | 219 | 171 | 194
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 3.4 | 17.9 | 2.1 | 27 | 405 | 796 | 0.443 | 0.28 | 0.4 | 0.57 | 0.68 | 6.6 | 3.2 | 348 | 247 | 228 | 273 | 208 | 236
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 3.4 | 19.4 | 2.1 | 29 | 580 | 902 | 0.32 | 0.31 | 0.38 | 0.55 | 0.65 | 9 | 3.2 | 434 | 311 | 278 | 333 | 248 | 281
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 3.4 | 20.9 | 2.1 | 30 | 600 | 1009 | 0.253 | 0.34 | 0.36 | 0.54 | 0.63 | 11.3 | 3.2 | 522 | 375 | 321 | 384 | 283 | 318
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 3.4 | 22.3 | 2.1 | 32 | 640 | 1193 | 0.206 | 0.36 | 0.35 | 0.51 | 0.6 | 14.2 | 5 | 644 | 479 | 364 | 432 | 315 | 350
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 3.4 | 23.9 | 2.1 | 33 | 660 | 1341 | 0.164 | 0.4 | 0.34 | 0.5 | 0.58 | 17.5 | 5 | 747 | 563 | 418 | 496 | 357 | 394
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 3.4 | 26.2 | 2.1 | 36 | 720 | 1546 | 0.125 | 0.44 | 0.33 | 0.48 | 0.56 | 22.7 | 5 | 909 | 699 | 494 | 583 | 413 | 452
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 3.4 | 28.3 | 2.1 | 38 | 760 | 1797 | 0.1 | 0.48 | 0.32 | 0.47 | 0.54 | 28.4 | 5 | 1098 | 865 | 568 | 666 | 466 | 506
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 3.4 | 31.4 | 2.1 | 41 | 820 | 2222 | 0.0778 | 0.54 | 0.3 | 0.45 | 0.5 | 37.8 | 7 | 1474 | 1241 | 660 | 755 | 529 | 558
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 3.4 | 34.6 | 2.1 | 44 | 880 | 2599 | 0.0605 | 0.61 | 0.29 | 0.44 | 0.48 | 47.3 | 7 | 1740 | 1525 | 767 | 868 | 602 | 627
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x630/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 3.4 | 38 | 2.1 | 47 | 940 | 3062 | 0.0469 | 0.67 | 0.27 | 0.43 | 0.46 | 59.6 | 7 | 2131 | 1895 | 861 | 913 | 690 | 666
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x800/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 3.4 | 42.3 | 2.4 | 52 | 1040 | 3686 | 0.0367 | 0.76 | 0.26 | 0.42 | 0.45 | 75.6 | 7 | 2673 | 2461 | 976 | 1017 | 764 | 728
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x1000/35 | 6/10 | 21 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 3.4 | 46.2 | 2.4 | 56 | 1120 | 4372 | 0.0291 | 0.84 | 0.25 | 0.4 | 0.42 | 94 | 7 | 3505 | 3157 | 1187 | 1270 | 852 | 842
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x35/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 7.2 | 5.5 | 19.5 | 2.1 | 29 | 435 | 1069 | 0.524 | 0.16 | 0.46 |  | 0.74 | 5 | 3.2 | 266 | 199 | 200 | 235 | 189 | 213
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 8.2 | 5.5 | 20.5 | 2.1 | 30 | 450 | 1203 | 0.387 | 0.17 | 0.45 |  | 0.72 | 7.1 | 3.2 | 383 | 288 | 239 | 282 | 222 | 250
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 31 | 465 | 1447 | 0.268 | 0.19 | 0.42 |  | 0.68 | 10 | 3.2 | 489 | 371 | 297 | 351 | 271 | 303
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 33 | 495 | 1718 | 0.193 | 0.21 | 0.4 |  | 0.66 | 13.6 | 3.2 | 613 | 470 | 361 | 426 | 323 | 360
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 34 | 510 | 2007 | 0.153 | 0.23 | 0.39 |  | 0.63 | 17.1 | 3.2 | 742 | 574 | 416 | 491 | 367 | 407
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 36 | 540 | 2364 | 0.124 | 0.25 | 0.37 |  | 0.6 | 21.4 | 5 | 920 | 747 | 470 | 549 | 409 | 445
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 37 | 555 | 2744 | 0.099 | 0.27 | 0.36 |  | 0.59 | 26.4 | 5 | 1079 | 892 | 538 | 625 | 461 | 498
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 18.3 | 5.5 | 30.6 | 2.1 | 40 | 600 | 3352 | 0.075 | 0.3 | 0.34 |  | 0.56 | 34.3 | 5 | 1344 | 1143 | 634 | 731 | 532 | 568
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 20.7 | 5.5 | 33 | 2.1 | 42 | 630 | 4032 | 0.06 | 0.35 | 0.33 |  | 0.54 | 42.9 | 5 | 1582 | 1364 | 724 | 830 | 599 | 633
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 45 | 675 | 4988 | 0.047 | 0.36 | 0.31 |  | 0.51 | 57.2 | 7 | 2327 | 2182 | 829 | 923 | 671 | 685
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 48 | 720 | 6080 | 0.037 | 0.43 | 0.3 |  | 0.49 | 71.4 | 7 | 2765 | 2689 | 953 | 1045 | 754 | 760
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x35/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 7.2 | 5.5 | 19.5 | 2.1 | 28 | 420 | 948 | 0.524 | 0.16 | 0.46 |  | 0.74 | 5 | 3.2 | 259 | 192 | 200 | 235 | 189 | 213
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 5.5 | 20.5 | 2.1 | 29 | 435 | 1078 | 0.387 | 0.17 | 0.44 |  | 0.72 | 7.1 | 3.2 | 373 | 278 | 239 | 282 | 222 | 250
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 31 | 465 | 1315 | 0.268 | 0.19 | 0.42 |  | 0.68 | 10 | 3.2 | 476 | 358 | 297 | 351 | 271 | 303
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 32 | 480 | 1579 | 0.193 | 0.21 | 0.4 |  | 0.66 | 13.6 | 3.2 | 598 | 454 | 361 | 426 | 323 | 360
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 34 | 510 | 1861 | 0.153 | 0.23 | 0.39 |  | 0.63 | 17.1 | 3.2 | 722 | 554 | 416 | 491 | 367 | 407
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 35 | 525 | 2212 | 0.124 | 0.25 | 0.37 |  | 0.6 | 21.4 | 5 | 897 | 723 | 470 | 549 | 409 | 445
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 37 | 555 | 2585 | 0.099 | 0.27 | 0.36 |  | 0.59 | 26.4 | 5 | 1048 | 861 | 538 | 625 | 461 | 498
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 5.5 | 30.6 | 2.1 | 39 | 585 | 3181 | 0.075 | 0.3 | 0.34 |  | 0.56 | 34.3 | 5 | 1283 | 1073 | 634 | 731 | 532 | 568
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 5.5 | 33 | 2.1 | 42 | 630 | 3763 | 0.06 | 0.33 | 0.33 |  | 0.54 | 42.9 | 5 | 1541 | 1309 | 724 | 830 | 599 | 633
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 44 | 660 | 4795 | 0.047 | 0.36 | 0.31 |  | 0.51 | 57.2 | 7 | 2279 | 2085 | 829 | 923 | 671 | 685
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 47 | 705 | 5872 | 0.037 | 0.43 | 0.3 |  | 0.49 | 71.4 | 7 | 2689 | 2576 | 953 | 1045 | 754 | 760
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x35/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 7.2 | 5.5 | 19.5 | 2.1 | 28 | 420 | 949 | 0.524 | 0.16 | 0.46 | 0.64 | 0.74 | 5 | 3.2 | 259 | 192 | 200 | 235 | 189 | 213
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 5.5 | 20.5 | 2.1 | 29 | 435 | 1079 | 0.387 | 0.17 | 0.44 | 0.62 | 0.72 | 7.1 | 3.2 | 374 | 278 | 239 | 282 | 222 | 250
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 31 | 465 | 1315 | 0.268 | 0.19 | 0.42 | 0.59 | 0.68 | 10 | 3.2 | 477 | 358 | 297 | 351 | 271 | 303
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 32 | 480 | 1580 | 0.193 | 0.21 | 0.4 | 0.57 | 0.66 | 13.6 | 3.2 | 600 | 458 | 361 | 426 | 323 | 360
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 34 | 510 | 1862 | 0.153 | 0.23 | 0.38 | 0.55 | 0.63 | 17.1 | 3.2 | 724 | 556 | 416 | 491 | 367 | 407
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 35 | 525 | 2212 | 0.124 | 0.25 | 0.37 | 0.53 | 0.6 | 21.4 | 5 | 903 | 730 | 470 | 549 | 409 | 445
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 37 | 555 | 2585 | 0.099 | 0.27 | 0.36 | 0.52 | 0.59 | 26.4 | 5 | 1068 | 871 | 538 | 625 | 461 | 498
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 5.5 | 30.6 | 2.1 | 39 | 585 | 3181 | 0.075 | 0.3 | 0.34 | 0.5 | 0.56 | 34.3 | 5 | 1309 | 1091 | 634 | 731 | 532 | 568
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 5.5 | 33 | 2.1 | 42 | 630 | 3851 | 0.06 | 0.33 | 0.33 | 0.48 | 0.54 | 42.9 | 5 | 1582 | 1350 | 724 | 830 | 599 | 633
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 44 | 660 | 4795 | 0.047 | 0.36 | 0.31 | 0.46 | 0.51 | 57.2 | 7 | 2255 | 2109 | 829 | 923 | 671 | 685
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 47 | 705 | 5873 | 0.037 | 0.4 | 0.3 | 0.45 | 0.49 | 71.4 | 7 | 2727 | 2614 | 953 | 1045 | 754 | 760
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 5.5 | 20.5 | 2.1 | 30 | 600 | 1166 | 0.387 | 0.17 | 0.45 |  | 0.72 | 7.1 | 3.2 | 369 | 276 | 239 | 282 | 222 | 250
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 32 | 640 | 1409 | 0.268 | 0.19 | 0.42 |  | 0.68 | 10 | 3.2 | 471 | 355 | 297 | 351 | 271 | 303
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 33 | 660 | 1675 | 0.193 | 0.21 | 0.41 |  | 0.66 | 13.6 | 3.2 | 591 | 451 | 361 | 426 | 323 | 360
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 35 | 700 | 1968 | 0.153 | 0.23 | 0.39 |  | 0.64 | 17.1 | 3.2 | 718 | 554 | 416 | 491 | 367 | 407
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 36 | 720 | 2320 | 0.124 | 0.25 | 0.37 |  | 0.6 | 21.4 | 5 | 897 | 723 | 470 | 549 | 409 | 445
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 38 | 760 | 2697 | 0.099 | 0.27 | 0.36 |  | 0.59 | 26.4 | 5 | 1063 | 871 | 538 | 625 | 461 | 498
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 5.5 | 30.6 | 2.1 | 40 | 800 | 3303 | 0.075 | 0.3 | 0.35 |  | 0.56 | 34.3 | 5 | 1300 | 1091 | 634 | 731 | 532 | 568
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 5.5 | 33 | 2.1 | 43 | 860 | 3978 | 0.06 | 0.32 | 0.34 |  | 0.55 | 42.9 | 5 | 1568 | 1350 | 724 | 830 | 599 | 633
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 45 | 900 | 4925 | 0.047 | 0.36 | 0.32 |  | 0.51 | 57.2 | 7 | 2230 | 2085 | 829 | 923 | 671 | 685
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - + 90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 49 | 980 | 6006 | 0.037 | 0.4 | 0.3 |  | 0.49 | 71.4 | 7 | 2727 | 2614 | 953 | 1045 | 754 | 760
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 8.3 | 5.5 | 20.5 | 2.1 | 29 | 435 | 936 | 0.641 | 0.17 | 0.44 | 0.62 | 0.72 | 4.7 | 3.2 | 276 | 204 | 185 | 219 | 172 | 195
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22 | 2.1 | 31 | 465 | 1037 | 0.443 | 0.19 | 0.42 | 0.6 | 0.69 | 6.6 | 3.2 | 351 | 261 | 231 | 273 | 210 | 237
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.5 | 2.1 | 32 | 480 | 1157 | 0.32 | 0.21 | 0.4 | 0.58 | 0.66 | 9 | 3.2 | 442 | 328 | 280 | 332 | 251 | 282
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25 | 2.1 | 34 | 510 | 1274 | 0.253 | 0.23 | 0.39 | 0.56 | 0.64 | 11.3 | 3.2 | 532 | 397 | 323 | 384 | 285 | 319
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.4 | 2.1 | 36 | 540 | 1491 | 0.206 | 0.25 | 0.37 | 0.54 | 0.61 | 14.2 | 5 | 653 | 500 | 366 | 432 | 319 | 352
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x185/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28 | 2.1 | 37 | 555 | 1546 | 0.164 | 0.27 | 0.36 | 0.53 | 0.6 | 17.5 | 3.2 | 753 | 570 | 420 | 494 | 361 | 396
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28 | 2.1 | 37 | 555 | 1636 | 0.164 | 0.27 | 0.36 | 0.52 | 0.59 | 17.5 | 5 | 760 | 590 | 420 | 494 | 361 | 396
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 18.1 | 5.5 | 30.3 | 2.1 | 39 | 585 | 1863 | 0.125 | 0.3 | 0.35 | 0.51 | 0.57 | 22.7 | 5 | 920 | 729 | 496 | 581 | 417 | 455
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 20.2 | 5.5 | 32.4 | 2.1 | 41 | 615 | 2084 | 0.1 | 0.32 | 0.33 | 0.49 | 0.55 | 28.4 | 5 | 1110 | 895 | 569 | 663 | 471 | 510
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.5 | 2.1 | 44 | 660 | 2567 | 0.0778 | 0.36 | 0.32 | 0.47 | 0.51 | 37.8 | 7 | 1474 | 1262 | 660 | 753 | 535 | 564
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.7 | 2.1 | 48 | 720 | 2992 | 0.0605 | 0.4 | 0.3 | 0.46 | 0.49 | 47.3 | 7 | 1724 | 1525 | 766 | 866 | 609 | 634
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x630/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 29.9 | 5.5 | 42.1 | 2.4 | 51 | 765 | 3520 | 0.0469 | 0.44 | 0.29 | 0.44 | 0.48 | 59.6 | 7 | 2105 | 1895 | 866 | 913 | 697 | 664
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x800/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 34.2 | 5.5 | 46.4 | 2.4 | 56 | 840 | 4182 | 0.0367 | 0.49 | 0.28 | 0.43 | 0.46 | 75.6 | 7 | 2546 | 2376 | 1000 | 1035 | 780 | 734
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x1000/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 38.1 | 5.5 | 50.3 | 2.4 | 61 | 915 | 5165 | 0.0291 | 0.54 | 0.27 | 0.42 | 0.44 | 94.6 | 7 | 3116 | 2917 | 1130 | 1168 | 868 | 809
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 5.5 | 20.6 | 2.1 | 29 | 435 | 795 | 0.641 | 0.17 | 0.44 | 0.62 | 0.72 | 4.7 | 3.2 | 269 | 198 | 185 | 219 | 172 | 195
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 31 | 465 | 888 | 0.443 | 0.19 | 0.42 | 0.59 | 0.69 | 6.6 | 3.2 | 344 | 254 | 231 | 273 | 210 | 237
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 32 | 480 | 999 | 0.32 | 0.21 | 0.4 | 0.57 | 0.66 | 9 | 3.2 | 433 | 321 | 280 | 332 | 251 | 282
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 34 | 510 | 1108 | 0.253 | 0.23 | 0.38 | 0.56 | 0.64 | 11.3 | 3.2 | 520 | 388 | 323 | 384 | 285 | 319
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 35 | 525 | 1301 | 0.206 | 0.25 | 0.37 | 0.54 | 0.61 | 14.2 | 5 | 643 | 495 | 366 | 432 | 319 | 352
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 37 | 555 | 1452 | 0.164 | 0.27 | 0.36 | 0.52 | 0.59 | 17.5 | 5 | 749 | 583 | 420 | 494 | 361 | 396
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 5.5 | 30.4 | 2.1 | 39 | 585 | 1671 | 0.125 | 0.3 | 0.34 | 0.5 | 0.56 | 22.7 | 5 | 913 | 726 | 496 | 581 | 417 | 455
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 5.5 | 32.5 | 2.1 | 41 | 615 | 1893 | 0.1 | 0.32 | 0.33 | 0.49 | 0.55 | 28.4 | 5 | 1098 | 883 | 569 | 663 | 471 | 510
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 44 | 660 | 2357 | 0.078 | 0.36 | 0.31 | 0.47 | 0.51 | 37.8 | 7 | 1485 | 1273 | 660 | 753 | 535 | 564
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 47 | 705 | 2757 | 0.061 | 0.4 | 0.3 | 0.45 | 0.49 | 47.3 | 7 | 1757 | 1541 | 766 | 866 | 609 | 634
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 5.5 | 42.2 | 2.4 | 51 | 765 | 3227 | 0.047 | 0.44 | 0.29 | 0.44 | 0.47 | 59.6 | 7 | 2131 | 1947 | 861 | 900 | 690 | 668
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 5.5 | 46.5 | 2.4 | 56 | 840 | 3856 | 0.037 | 0.49 | 0.28 | 0.43 | 0.45 | 75.6 | 7 | 2673 | 2503 | 976 | 1008 | 764 | 731
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 5.5 | 50.4 | 2.4 | 61 | 915 | 4824 | 0.0291 | 0.55 | 0.28 | 0.42 | 0.45 | 94 | 7 | 4323 | 3771 | 1187 | 1262 | 863 | 852
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 5.5 | 20.5 | 2.1 | 29 | 435 | 780 | 0.641 | 0.17 | 0.44 | 0.62 | 0.72 | 4.7 | 3.2 | 269 | 198 | 185 | 219 | 172 | 195
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22 | 2.1 | 30 | 450 | 873 | 0.443 | 0.19 | 0.42 | 0.59 | 0.69 | 6.6 | 3.2 | 344 | 254 | 231 | 273 | 210 | 237
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.5 | 2.1 | 32 | 480 | 984 | 0.32 | 0.21 | 0.4 | 0.57 | 0.66 | 9 | 3.2 | 433 | 321 | 280 | 332 | 251 | 282
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25 | 2.1 | 33 | 495 | 1093 | 0.253 | 0.23 | 0.39 | 0.56 | 0.64 | 11.3 | 3.2 | 518 | 387 | 323 | 384 | 285 | 319
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.4 | 2.1 | 35 | 525 | 1282 | 0.206 | 0.25 | 0.37 | 0.54 | 0.61 | 14.2 | 5 | 638 | 485 | 366 | 432 | 319 | 352
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28 | 2.1 | 36 | 540 | 1434 | 0.164 | 0.27 | 0.36 | 0.52 | 0.59 | 17.5 | 5 | 749 | 583 | 420 | 494 | 361 | 396
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 5.5 | 30.3 | 2.1 | 39 | 585 | 1647 | 0.125 | 0.3 | 0.34 | 0.5 | 0.56 | 22.7 | 5 | 909 | 722 | 496 | 581 | 417 | 455
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 5.5 | 32.4 | 2.1 | 41 | 615 | 1869 | 0.1 | 0.32 | 0.33 | 0.49 | 0.55 | 28.4 | 5 | 1098 | 883 | 569 | 663 | 471 | 510
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.5 | 2.1 | 44 | 660 | 2321 | 0.0778 | 0.36 | 0.31 | 0.47 | 0.51 | 37.8 | 7 | 1485 | 1273 | 660 | 753 | 535 | 564
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.7 | 2.1 | 47 | 705 | 2728 | 0.0605 | 0.4 | 0.3 | 0.45 | 0.49 | 47.3 | 7 | 1757 | 1541 | 766 | 866 | 609 | 634
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 5.5 | 42.1 | 2.4 | 51 | 765 | 3227 | 0.0469 | 0.44 | 0.29 | 0.44 | 0.47 | 59.6 | 7 | 2131 | 1947 | 861 | 900 | 690 | 668
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 5.5 | 46.4 | 2.4 | 55 | 825 | 3846 | 0.0367 | 0.49 | 0.28 | 0.43 | 0.45 | 75.6 | 7 | 2673 | 2503 | 976 | 1008 | 764 | 731
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 5.5 | 50.3 | 2.4 | 60 | 900 | 4634 | 0.0291 | 0.54 | 0.26 | 0.42 | 0.44 | 94.6 | 7 | 3315 | 3249 | 1095 | 1107 | 837 | 770
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 5.5 | 20.6 | 2.1 | 30 | 600 | 876 | 0.641 | 0.17 | 0.45 | 0.62 | 0.72 | 4.7 | 3.2 | 266 | 196 | 185 | 219 | 172 | 195
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 5.5 | 22.1 | 2.1 | 32 | 640 | 982 | 0.443 | 0.19 | 0.42 | 0.6 | 0.69 | 6.6 | 3.2 | 339 | 251 | 231 | 273 | 210 | 237
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 5.5 | 23.6 | 2.1 | 33 | 660 | 1101 | 0.32 | 0.21 | 0.41 | 0.58 | 0.66 | 9 | 3.2 | 426 | 318 | 280 | 332 | 251 | 282
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 5.5 | 25.1 | 2.1 | 35 | 700 | 1217 | 0.253 | 0.23 | 0.39 | 0.56 | 0.64 | 11.3 | 3.2 | 515 | 386 | 323 | 384 | 285 | 319
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 5.5 | 26.5 | 2.1 | 36 | 720 | 1412 | 0.206 | 0.25 | 0.38 | 0.54 | 0.61 | 14.2 | 5 | 634 | 488 | 366 | 432 | 319 | 352
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 5.5 | 28.1 | 2.1 | 38 | 760 | 1568 | 0.164 | 0.27 | 0.36 | 0.53 | 0.59 | 17.5 | 5 | 733 | 574 | 420 | 494 | 361 | 396
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 5.5 | 30.4 | 2.1 | 40 | 800 | 1792 | 0.125 | 0.3 | 0.35 | 0.51 | 0.57 | 22.7 | 5 | 897 | 714 | 496 | 581 | 417 | 455
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 5.5 | 32.5 | 2.1 | 42 | 840 | 2020 | 0.1 | 0.32 | 0.34 | 0.5 | 0.55 | 28.4 | 5 | 1080 | 877 | 569 | 663 | 471 | 510
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 5.5 | 35.6 | 2.1 | 45 | 900 | 2493 | 0.078 | 0.36 | 0.32 | 0.47 | 0.51 | 37.8 | 7 | 1474 | 1273 | 660 | 753 | 535 | 564
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 49 | 980 | 2903 | 0.061 | 0.4 | 0.3 | 0.46 | 0.49 | 47.3 | 7 | 1740 | 1541 | 766 | 866 | 609 | 634
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/50 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 5.5 | 38.8 | 2.1 | 49 | 980 | 3059 | 0.061 | 0.4 | 0.3 | 0.44 | 0.48 | 47.3 | 10 | 1840 | 1707 | 766 | 866 | 609 | 634
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x630/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 5.5 | 42.2 | 2.4 | 52 | 780 | 3383 | 0.047 | 0.44 | 0.29 | 0.44 | 0.48 | 59.6 | 7 | 2105 | 1947 | 866 | 900 | 705 | 668
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x800/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 5.5 | 46.5 | 2.4 | 56 | 840 | 3858 | 0.037 | 0.49 | 0.28 | 0.43 | 0.46 | 75.6 | 7 | 2631 | 2503 | 984 | 1008 | 767 | 734
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x1000/35 | 12/20 | 42 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 5.5 | 50.4 | 2.4 | 61 | 1220 | 4824 | 0.0291 | 0.55 | 0.28 | 0.42 | 0.45 | 94 | 7 | 4323 | 3771 | 1187 | 1262 | 863 | 852
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 8.2 | 8 | 25.5 | 2.1 | 35 | 525 | 1439 | 0.387 | 0.13 | 0.48 |  | 0.73 | 7.1 | 3.2 | 367 | 288 | 241 | 282 | 225 | 251
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 36 | 540 | 1697 | 0.268 | 0.15 | 0.45 |  | 0.7 | 10 | 3.2 | 476 | 374 | 299 | 350 | 274 | 304
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 38 | 570 | 1979 | 0.193 | 0.16 | 0.43 |  | 0.67 | 13.6 | 3.2 | 598 | 476 | 363 | 425 | 327 | 362
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 39 | 585 | 2279 | 0.153 | 0.17 | 0.41 |  | 0.64 | 17.1 | 3.2 | 729 | 585 | 418 | 468 | 371 | 409
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 41 | 615 | 2648 | 0.124 | 0.19 | 0.4 |  | 0.62 | 21.4 | 5 | 910 | 760 | 472 | 548 | 414 | 449
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 42 | 630 | 3036 | 0.099 | 0.2 | 0.38 |  | 0.6 | 26.4 | 5 | 1073 | 913 | 539 | 624 | 466 | 502
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 18.3 | 8 | 35.6 | 2.1 | 45 | 675 | 3661 | 0.075 | 0.22 | 0.36 |  | 0.57 | 34.3 | 5 | 1318 | 1143 | 635 | 728 | 539 | 574
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 20.7 | 8 | 38 | 2.1 | 47 | 705 | 4368 | 0.06 | 0.24 | 0.35 |  | 0.55 | 42.9 | 5 | 1595 | 1405 | 725 | 828 | 606 | 640
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 50 | 750 | 5347 | 0.047 | 0.26 | 0.34 |  | 0.52 | 57.2 | 7 | 2255 | 2182 | 831 | 922 | 680 | 695
N2XSY | Copper | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 53 | 795 | 6472 | 0.037 | 0.29 | 0.32 |  | 0.5 | 71.4 | 7 | 2727 | 2727 | 953 | 1045 | 765 | 773
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 8 | 25.5 | 2.1 | 34 | 510 | 1292 | 0.387 | 0.13 | 0.48 |  | 0.73 | 7.1 | 3.2 | 359 | 280 | 241 | 282 | 225 | 251
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 36 | 540 | 1542 | 0.268 | 0.15 | 0.45 |  | 0.7 | 10 | 3.2 | 466 | 364 | 299 | 350 | 274 | 304
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 37 | 555 | 1817 | 0.193 | 0.16 | 0.43 |  | 0.67 | 13.6 | 3.2 | 585 | 462 | 363 | 425 | 327 | 362
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 39 | 585 | 2110 | 0.153 | 0.17 | 0.41 |  | 0.64 | 17.1 | 3.2 | 711 | 567 | 418 | 468 | 371 | 409
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 40 | 600 | 2473 | 0.124 | 0.19 | 0.4 |  | 0.62 | 21.4 | 5 | 890 | 740 | 472 | 548 | 414 | 449
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 42 | 630 | 2853 | 0.099 | 0.2 | 0.38 |  | 0.6 | 26.4 | 5 | 1048 | 882 | 539 | 624 | 466 | 502
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 8 | 35.6 | 2.1 | 44 | 660 | 3467 | 0.075 | 0.22 | 0.36 |  | 0.57 | 34.3 | 5 | 1283 | 1108 | 635 | 728 | 539 | 574
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 8 | 38 | 2.1 | 47 | 705 | 4164 | 0.06 | 0.24 | 0.35 |  | 0.55 | 42.9 | 5 | 1555 | 1364 | 725 | 828 | 606 | 640
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 49 | 735 | 5131 | 0.047 | 0.26 | 0.34 |  | 0.52 | 57.2 | 7 | 2206 | 2109 | 831 | 922 | 680 | 695
N2XS2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 53 | 795 | 6234 | 0.037 | 0.29 | 0.32 |  | 0.5 | 71.4 | 7 | 2689 | 2652 | 953 | 1045 | 765 | 773
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 8 | 25.5 | 2.1 | 34 | 510 | 1292 | 0.387 | 0.13 | 0.48 |  | 0.73 | 7.1 | 3.2 | 365 | 283 | 241 | 282 | 225 | 251
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 36 | 540 | 1542 | 0.268 | 0.15 | 0.45 |  | 0.7 | 10 | 3.2 | 466 | 364 | 299 | 350 | 274 | 304
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 37 | 555 | 1818 | 0.193 | 0.16 | 0.43 |  | 0.67 | 13.6 | 3.2 | 589 | 464 | 363 | 425 | 327 | 362
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 39 | 585 | 2110 | 0.153 | 0.17 | 0.41 |  | 0.64 | 17.1 | 3.2 | 713 | 567 | 418 | 468 | 371 | 409
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 40 | 600 | 2473 | 0.124 | 0.19 | 0.4 |  | 0.62 | 21.4 | 5 | 893 | 740 | 472 | 548 | 414 | 449
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 42 | 630 | 2854 | 0.099 | 0.2 | 0.38 |  | 0.6 | 26.4 | 5 | 1048 | 887 | 539 | 624 | 466 | 502
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 8 | 35.6 | 2.1 | 44 | 660 | 3468 | 0.075 | 0.22 | 0.36 |  | 0.57 | 34.3 | 5 | 1283 | 1117 | 635 | 728 | 539 | 574
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 8 | 38 | 2.1 | 47 | 705 | 4164 | 0.06 | 0.24 | 0.35 |  | 0.55 | 42.9 | 5 | 1555 | 1364 | 725 | 828 | 606 | 640
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 49 | 735 | 5131 | 0.047 | 0.26 | 0.33 |  | 0.52 | 57.2 | 7 | 2206 | 2109 | 831 | 922 | 680 | 695
N2XS(F)2Y | Copper | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 53 | 795 | 6235 | 0.037 | 0.29 | 0.32 |  | 0.5 | 71.4 | 7 | 2689 | 2652 | 953 | 1045 | 765 | 773
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.2 | 8 | 25.5 | 2.1 | 35 | 700 | 1405 | 0.387 | 0.13 | 0.48 |  | 0.73 | 7.1 | 3.2 | 360 | 280 | 241 | 282 | 225 | 251
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 37 | 740 | 1646 | 0.268 | 0.15 | 0.45 |  | 0.7 | 10 | 3.2 | 462 | 362 | 299 | 350 | 274 | 304
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 38 | 760 | 1926 | 0.193 | 0.16 | 0.43 |  | 0.67 | 13.6 | 3.2 | 583 | 459 | 363 | 425 | 327 | 362
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 40 | 800 | 2227 | 0.153 | 0.17 | 0.42 |  | 0.65 | 17.1 | 3.2 | 707 | 563 | 418 | 468 | 371 | 409
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 41 | 820 | 2590 | 0.124 | 0.19 | 0.4 |  | 0.62 | 21.4 | 5 | 876 | 730 | 472 | 548 | 414 | 449
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 43 | 860 | 2975 | 0.099 | 0.2 | 0.39 |  | 0.6 | 26.4 | 5 | 1032 | 876 | 539 | 624 | 466 | 502
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.3 | 8 | 35.6 | 2.1 | 45 | 900 | 3594 | 0.075 | 0.22 | 0.37 |  | 0.58 | 34.3 | 5 | 1274 | 1108 | 635 | 728 | 539 | 574
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.7 | 8 | 38 | 2.1 | 48 | 960 | 4300 | 0.06 | 0.24 | 0.36 |  | 0.56 | 42.9 | 5 | 1541 | 1377 | 725 | 828 | 606 | 640
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 51 | 1020 | 5290 | 0.047 | 0.26 | 0.34 |  | 0.52 | 57.2 | 7 | 2206 | 2109 | 831 | 922 | 680 | 695
N2XS(FL)2Y | Copper | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 54 | 1080 | 6403 | 0.037 | 0.29 | 0.32 |  | 0.5 | 71.4 | 7 | 2689 | 2652 | 953 | 1045 | 765 | 773
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 8.3 | 8 | 25.5 | 2.1 | 34 | 510 | 1176 | 0.641 | 0.13 | 0.48 | 0.65 | 0.73 | 4.7 | 3.2 | 269 | 206 | 187 | 219 | 174 | 195
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 9.8 | 8 | 27 | 2.1 | 36 | 540 | 1290 | 0.443 | 0.15 | 0.45 | 0.63 | 0.7 | 6.6 | 3.2 | 344 | 264 | 232 | 273 | 213 | 238
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.5 | 2.1 | 37 | 555 | 1421 | 0.32 | 0.16 | 0.43 | 0.61 | 0.67 | 9 | 3.2 | 433 | 334 | 282 | 331 | 254 | 283
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 12.8 | 8 | 30 | 2.1 | 39 | 585 | 1548 | 0.253 | 0.17 | 0.41 | 0.58 | 0.65 | 11.3 | 3.2 | 530 | 408 | 325 | 382 | 289 | 321
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.4 | 2.1 | 40 | 600 | 1757 | 0.206 | 0.19 | 0.4 | 0.57 | 0.62 | 14.2 | 5 | 640 | 509 | 367 | 429 | 322 | 354
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 15.8 | 8 | 33 | 2.1 | 42 | 630 | 1930 | 0.164 | 0.2 | 0.39 | 0.55 | 0.6 | 17.5 | 5 | 744 | 599 | 421 | 492 | 364 | 399
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 18.1 | 8 | 35.3 | 2.1 | 44 | 660 | 2172 | 0.125 | 0.22 | 0.37 | 0.53 | 0.58 | 22.7 | 5 | 905 | 737 | 496 | 578 | 422 | 458
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 20.2 | 8 | 37.4 | 2.1 | 46 | 690 | 2424 | 0.1 | 0.24 | 0.35 | 0.52 | 0.56 | 28.4 | 5 | 1092 | 907 | 568 | 659 | 476 | 514
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.5 | 2.1 | 49 | 735 | 2928 | 0.0778 | 0.27 | 0.34 | 0.49 | 0.53 | 37.8 | 7 | 1453 | 1284 | 659 | 750 | 541 | 570
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.7 | 2.4 | 53 | 795 | 3390 | 0.0605 | 0.29 | 0.33 | 0.48 | 0.5 | 47.3 | 7 | 1724 | 1541 | 764 | 861 | 616 | 642
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x630/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 29.9 | 8 | 47.1 | 2.4 | 56 | 840 | 3937 | 0.0469 | 0.32 | 0.31 | 0.46 | 0.49 | 59.6 | 7 | 2052 | 1921 | 877 | 907 | 702 | 672
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x800/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 34.2 | 8 | 51.4 | 2.9 | 61 | 915 | 4667 | 0.0367 | 0.36 | 0.3 | 0.45 | 0.47 | 75.6 | 7 | 2546 | 2461 | 1000 | 1017 | 780 | 742
NA2XSY | Aluminum | XLPE | Yes | Yes | Yes | No | PVC | 1x1000/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -25 | -5 | uncoloured | red or black | EN 60 332-1-2 | Eca | wooden or metal drums | yes | RM | 38.1 | 8 | 55.3 | 3 | 67 | 1005 | 5703 | 0.0291 | 0.39 | 0.29 | 0.44 | 0.45 | 94.6 | 7 | 3050 | 3050 | 1142 | 1142 | 877 | 824
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 8 | 25.6 | 2.1 | 34 | 510 | 1009 | 0.641 | 0.13 | 0.48 | 0.65 | 0.73 | 4.7 | 3.2 | 263 | 202 | 187 | 219 | 174 | 195
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 36 | 540 | 1115 | 0.443 | 0.15 | 0.45 | 0.62 | 0.7 | 6.6 | 3.2 | 337 | 258 | 232 | 273 | 213 | 238
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 37 | 555 | 1237 | 0.32 | 0.16 | 0.43 | 0.6 | 0.67 | 9 | 3.2 | 424 | 327 | 282 | 331 | 254 | 283
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 39 | 585 | 1357 | 0.253 | 0.17 | 0.41 | 0.58 | 0.64 | 11.3 | 3.2 | 520 | 400 | 325 | 382 | 289 | 321
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 40 | 600 | 1561 | 0.206 | 0.19 | 0.4 | 0.56 | 0.62 | 14.2 | 5 | 631 | 501 | 367 | 429 | 322 | 354
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 42 | 630 | 1721 | 0.164 | 0.2 | 0.39 | 0.55 | 0.6 | 17.5 | 5 | 733 | 592 | 421 | 492 | 364 | 399
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 8 | 35.4 | 2.1 | 44 | 660 | 1956 | 0.125 | 0.22 | 0.37 | 0.53 | 0.58 | 22.7 | 5 | 897 | 733 | 496 | 578 | 422 | 458
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 8 | 37.5 | 2.1 | 46 | 690 | 2203 | 0.1 | 0.24 | 0.36 | 0.52 | 0.56 | 28.4 | 5 | 1068 | 895 | 568 | 659 | 476 | 514
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 49 | 735 | 2693 | 0.078 | 0.26 | 0.34 | 0.49 | 0.52 | 37.8 | 7 | 1453 | 1294 | 659 | 750 | 541 | 570
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 53 | 795 | 3119 | 0.061 | 0.29 | 0.32 | 0.48 | 0.5 | 47.3 | 7 | 1740 | 1575 | 764 | 861 | 616 | 642
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 8 | 47.2 | 2.4 | 56 | 840 | 3617 | 0.047 | 0.32 | 0.31 | 0.46 | 0.48 | 59.6 | 7 | 2131 | 2000 | 861 | 889 | 690 | 668
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 8 | 51.5 | 2.4 | 61 | 915 | 4300 | 0.037 | 0.36 | 0.3 | 0.45 | 0.46 | 75.6 | 7 | 2631 | 2546 | 984 | 1000 | 770 | 734
NA2XS2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 8 | 55.4 | 2.4 | 67 | 1005 | 5326 | 0.0291 | 0.39 | 0.3 | 0.44 | 0.45 | 94 | 7 | 3302 | 3152 | 1196 | 1256 | 878 | 863
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 8 | 25.5 | 2.1 | 34 | 510 | 988 | 0.641 | 0.13 | 0.48 | 0.65 | 0.73 | 4.7 | 3.2 | 263 | 202 | 187 | 219 | 174 | 195
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27 | 2.1 | 35 | 525 | 1094 | 0.443 | 0.15 | 0.45 | 0.62 | 0.7 | 6.6 | 3.2 | 337 | 258 | 232 | 273 | 213 | 238
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.5 | 2.1 | 37 | 555 | 1216 | 0.32 | 0.16 | 0.43 | 0.6 | 0.67 | 9 | 3.2 | 425 | 327 | 282 | 331 | 254 | 283
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30 | 2.1 | 38 | 570 | 1335 | 0.253 | 0.17 | 0.41 | 0.58 | 0.65 | 11.3 | 3.2 | 510 | 395 | 325 | 382 | 289 | 321
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.4 | 2.1 | 40 | 600 | 1535 | 0.206 | 0.19 | 0.4 | 0.56 | 0.62 | 14.2 | 5 | 632 | 504 | 367 | 429 | 322 | 354
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33 | 2.1 | 41 | 615 | 1699 | 0.164 | 0.2 | 0.38 | 0.55 | 0.6 | 17.5 | 5 | 735 | 594 | 421 | 492 | 364 | 399
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 8 | 35.3 | 2.1 | 44 | 660 | 1928 | 0.125 | 0.22 | 0.37 | 0.53 | 0.58 | 22.7 | 5 | 897 | 737 | 496 | 578 | 422 | 458
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 8 | 37.4 | 2.1 | 46 | 690 | 2167 | 0.1 | 0.24 | 0.35 | 0.51 | 0.56 | 28.4 | 5 | 1080 | 907 | 568 | 659 | 476 | 514
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.5 | 2.1 | 49 | 735 | 2654 | 0.0778 | 0.26 | 0.34 | 0.49 | 0.53 | 37.8 | 5 | 1453 | 1230 | 659 | 750 | 541 | 570
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.7 | 2.4 | 52 | 780 | 3087 | 0.0605 | 0.29 | 0.32 | 0.48 | 0.5 | 47.3 | 7 | 1740 | 1591 | 764 | 861 | 616 | 642
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x630/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 8 | 47.1 | 2.4 | 56 | 840 | 3603 | 0.0469 | 0.32 | 0.31 | 0.46 | 0.48 | 59.6 | 7 | 2105 | 2000 | 866 | 889 | 692 | 653
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x800/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 8 | 51.4 | 2.4 | 60 | 900 | 4284 | 0.0367 | 0.36 | 0.3 | 0.45 | 0.46 | 75.6 | 7 | 2631 | 2546 | 984 | 1000 | 770 | 734
NA2XS(F)2Y | Aluminum | XLPE | Yes | Yes | Yes | No | PE | 1x1000/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 8 | 55.3 | 2.4 | 65 | 975 | 5093 | 0.0291 | 0.39 | 0.28 | 0.44 | 0.45 | 94.6 | 7 | 3315 | 3381 | 1095 | 1085 | 841 | 784
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x50/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 8.3 | 8 | 25.6 | 2.1 | 35 | 700 | 1100 | 0.641 | 0.13 | 0.48 | 0.65 | 0.73 | 4.7 | 3.2 | 261 | 200 | 187 | 219 | 174 | 195
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x70/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 9.8 | 8 | 27.1 | 2.1 | 37 | 740 | 1213 | 0.443 | 0.15 | 0.45 | 0.63 | 0.7 | 6.6 | 3.2 | 334 | 257 | 232 | 273 | 213 | 238
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x95/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 11.3 | 8 | 28.6 | 2.1 | 38 | 760 | 1339 | 0.32 | 0.16 | 0.43 | 0.61 | 0.67 | 9 | 3.2 | 420 | 325 | 282 | 331 | 254 | 283
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x120/16 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 12.8 | 8 | 30.1 | 2.1 | 40 | 800 | 1463 | 0.253 | 0.17 | 0.42 | 0.59 | 0.65 | 11.3 | 3.2 | 506 | 393 | 325 | 382 | 289 | 321
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x150/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 14.2 | 8 | 31.5 | 2.1 | 41 | 820 | 1660 | 0.206 | 0.19 | 0.4 | 0.57 | 0.62 | 14.2 | 5 | 625 | 500 | 367 | 429 | 322 | 354
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x185/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 15.8 | 8 | 33.1 | 2.1 | 43 | 860 | 1837 | 0.164 | 0.2 | 0.39 | 0.55 | 0.6 | 17.5 | 5 | 726 | 590 | 421 | 492 | 364 | 399
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x240/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 18.1 | 8 | 35.4 | 2.1 | 45 | 900 | 2049 | 0.125 | 0.22 | 0.37 | 0.53 | 0.58 | 22.7 | 5 | 890 | 733 | 496 | 578 | 422 | 458
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x300/25 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 20.2 | 8 | 37.5 | 2.1 | 47 | 940 | 2336 | 0.1 | 0.24 | 0.36 | 0.52 | 0.56 | 28.4 | 5 | 1062 | 889 | 568 | 659 | 476 | 514
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x400/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 23.3 | 8 | 40.6 | 2.1 | 50 | 1000 | 2842 | 0.0778 | 0.27 | 0.34 | 0.49 | 0.52 | 37.8 | 7 | 1453 | 1305 | 659 | 750 | 541 | 570
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x500/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 26.5 | 8 | 43.8 | 2.4 | 54 | 1080 | 3269 | 0.0605 | 0.29 | 0.32 | 0.48 | 0.5 | 47.3 | 7 | 1724 | 1575 | 764 | 861 | 616 | 642
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x630/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 29.9 | 8 | 47.2 | 2.4 | 56 | 1120 | 3590 | 0.0469 | 0.32 | 0.31 | 0.46 | 0.48 | 59.6 | 7 | 2105 | 2000 | 866 | 889 | 692 | 653
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x800/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 34.2 | 8 | 51.5 | 2.4 | 60 | 1200 | 4284 | 0.0367 | 0.36 | 0.3 | 0.45 | 0.46 | 75.6 | 7 | 2631 | 2546 | 984 | 1000 | 770 | 731
NA2XS(FL)2Y | Aluminum | XLPE | Yes | Yes | Yes | Yes | PE | 1x1000/35 | 18/30 | 63 | +90 | +250 | -35 - +90 | -35 | -20 | uncoloured | black | no | Fca | wooden or metal drums | yes | RM | 38.1 | 8 | 55.4 | 2.4 | 67 | 1340 | 5327 | 0.0291 | 0.39 | 0.3 | 0.44 | 0.45 | 94 | 7 | 3302 | 3152 | 1196 | 1256 | 878 | 863