## Sheet1
Part Number | Conductor | Insulation | CUScreen | Sheath | Number of cores and cross-section | Rated voltage | Test voltage | Maximal short-circuit temperature | Maximal operating conductor temperature | Minimal temperature for laying | Minimal storage temperature | Operating temperature range | Colour of insulation | Colour of sheath | Self-extinguishing of single cable | CPR class | Packaging | RoHS/REACH | Bending radius | Shape of conductor | Nominal insulation thickness | Nominal sheath thickness | Outer diameter (approx.) | Weight (approx.) | Maximum resistance of conductor
Units |  |  |  |  | mm2 | kV | kV | °C | °C | °C | °C | °C | [8 empty] | mm | mm | mm | kg/km | Ohm/km
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x1,5 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 22 | RM |  |  | 4,50 | 33 | 13.7
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x2,5 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 24 | RM |  |  | 4,90 | 41 | 8.21
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x4 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 26 | RM |  |  | 5,50 | 57 | 5.09
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x6 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 30 | RM |  |  | 5,90 | 73 | 3.39
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x10 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 35 | RM |  |  | 6,90 | 110 | 1.95
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x16 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 40 | RM |  |  | 8,00 | 170 | 1.24
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x25 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 50 | RM |  |  | 10,00 | 260 | 0.795
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x35 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 56 | RM |  |  | 11,00 | 360 | 0.565
H1Z2Z2-K | tinned CU | Halogen free | No | Halogen free | 1x50 | AC: 1000 / 1000 V DC: 1500 V | 6,5 kV AC, 15 kV DC (5 min.) | +250°C Max. 5 sec. | 120 | -25 |  | -40°C / +90°C |  | black or red |  |  | cable coils/cable drums | yes/yes | 60 | RM |  |  | 13,20 | 500 | 0.393